## OSBL_IO_List_SCS_v4
Status_Comment | Код | Title | LOOP | TYPNO | Loop No | Logic No | Tag No | Service | Instrument Type | FCS | PID No | Location | I/O Type | Extype | System | Sub System | Auxiliary Instrument | Min | Max | Unit | Min1 | Max1 | Unit1 | LL | L | H | HH | Unit2 | Rev | Remarks | 包设备 | Поле28 | Поле29 | Doc | REV_AK | CABLE No_AK | Discription_AK | Cable type | Beginning | Ending | Length(m) | Color | Pair | Note | Title_AK | Drum No | Power supply voltage | CABLE No_Tecon | MCC substations | Control_cabinet | Mashalling_cabinet | Тег_CPU | Main_Chassis | Redundand_Chassis | Slot | Redundant_slot | Main_module | Main_module2 | Redundant_module | Redundant_module2 | Channel | ModuleType
| 1 | 1401 | 2701-XZY-10101A | SDO0001-01 | 2701-X-10101A | 2701-Z-10001/2701-Z-10004/2701-Z-10101 | 2701-XZY-10101A | Styrene Inlet Switch Valve of 2701-TK-1205A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10101 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 01 | Rev3 JB No. Change | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 20 | DO32P
| 2 | 1401 | 2701-XZZSC-10101A | SDI0010-02R | 2701-X-10101A | - | 2701-XZZSC-10101A | Styrene Inlet Switch Valve of 2701-TK-1205A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 18 | DI32
| 3 | 1401 | 2701-XZZSO-10101A | SDI0010-02R | 2701-X-10101A | - | 2701-XZZSO-10101A | Styrene Inlet Switch Valve of 2701-TK-1205A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 06 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 19 | DI32
| 5 | 1401 | 2701-XZY-10102A | SDO0001-01 | 2701-X-10102A | 2701-Z-10001/2701-Z-10004/2701-Z-10102 | 2701-XZY-10102A | Styrene Outlet Switch Valve of 2701-TK-1205A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 04 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 21 | DO32P
| 6 | 1401 | 2701-XZZSC-10102A | SDI0010-02R | 2701-X-10102A | 2701-Z-10102 | 2701-XZZSC-10102A | Styrene Outlet Switch Valve of 2701-TK-1205A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 04 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 9 | DI32
| 8 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 01 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 0 | AI16H
| 9 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | - | 2701-LZIA-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 10 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | - | 2701-LZAHH-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 11 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | - | 2701-LZALL-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 13 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 08 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 8 | AI16H
| 14 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | - | 2701-LZIA-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 15 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | - | 2701-LZAHH-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 16 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | - | 2701-LZALL-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
Изм 2026.06.19 Change io type DIR-VFC -> S | 18 | 1401 | 2701-HZS-10001 | SDO0001-01 | 2701-HZS-10001 | 2701-Z-10001 | 2701-HZS-10001 | Fire dike isolation interlock 1 | Soft Push button | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change to soft button |  |  | Z-10001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN
| 19 | 1401 | 2701-HZS-10002 | SDI0010-01R | 2701-HZS-10002 | 2701-Z-10001 | 2701-HZS-10002 | Manual confirmation | PUSH BUTTON | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B042/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2701-S-JB-B042 | SIS |  | BK | 01 | Rev3 JB No. Change | 1401 |  |  | 2701-S-JB-B042 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 1 | DI32
Изм 2026.06.19 Change tag 2701-HZS-10007 -> 0005-HZS-10007 | 20 | 005 | 0005-HZS-10007-1 | SDI0010-01R | 0005-HZS-10007 | 2701-Z-10004 | 0005-HZS-10007-1 | Process block interlock (ESD-2) | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1401-PR007-0101A | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change tag no |  |  | Z-10004 | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 0 | DI32
| 22 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 02 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 1 | AI16H
| 23 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | - | 2701-LZIA-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 24 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | - | 2701-LZAHH-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 25 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | - | 2701-LZALL-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 27 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 91,51 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 01 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 13 | AI16H
| 28 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | - | 2701-LZIA-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 29 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | - | 2701-LZAHH-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 30 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | - | 2701-LZALL-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 32 | 1401 | 2701-XZY-10101B | SDO0001-01 | 2701-X-10101B | 2701-Z-10001/2701-Z-10004/2701-Z-10101 | 2701-XZY-10101B | Styrene Inlet Switch Valve of 2701-TK-1205B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10101 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 02 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 16 | DO32P
| 33 | 1401 | 2701-XZZSC-10101B | SDI0010-02R | 2701-X-10101B | - | 2701-XZZSC-10101B | Styrene Inlet Switch Valve of 2701-TK-1205B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 02 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 20 | DI32
| 34 | 1401 | 2701-XZZSO-10101B | SDI0010-02R | 2701-X-10101B | - | 2701-XZZSO-10101B | Styrene Inlet Switch Valve of 2701-TK-1205B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 07 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 21 | DI32
| 36 | 1401 | 2701-XZY-10102B | SDO0001-01 | 2701-X-10102B | 2701-Z-10001/2701-Z-10004/2701-Z-10102 | 2701-XZY-10102B | Styrene Inlet Switch Valve of 2701-TK-1205B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 05 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 17 | DO32P
| 37 | 1401 | 2701-XZZSC-10102B | SDI0010-02R | 2701-X-10102B | 2701-Z-10102 | 2701-XZZSC-10102B | Styrene Inlet Switch Valve of 2701-TK-1205B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 11 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 7 | DI32
| 40 | 1401 | 2701-LZIA-10101C | SAI1000-01R | 2701-L-10101C | 2701-Z-10101/2701-Z-10102/2701-Z-10103 | 2701-LZT-10101C | Remote Liquid Level Gauge of 2701-TK-1205S | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10101/10102/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 03 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 2 | AI16H
| 41 | 1401 | 2701-LZIA-10101C | SAI1000-01R | 2701-L-10101C | - | 2701-LZIA-10101C | Remote Liquid Level Gauge of 2701-TK-1205S | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 42 | 1401 | 2701-LZIA-10101C | SAI1000-01R | 2701-L-10101C | - | 2701-LZAH-10101C | Remote Liquid Level Gauge of 2701-TK-1205S | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 44 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | 2701-Z-10101/2701-Z-10102/2701-Z-10103 | 2701-LZT-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 91,51 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10101/10102/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 07 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 15 | AI16H
| 45 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | - | 2701-LZIA-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 46 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | - | 2701-LZAHH-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 47 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | - | 2701-LZALL-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 49 | 1401 | 2701-XZY-10101C | SDO0001-01 | 2701-X-10101C | 2701-Z-10001/2701-Z-10004/2701-Z-10101 | 2701-XZY-10101C | Styrene Inlet Switch Valve of 2701-TK-1205S | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10101 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 03 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 22 | DO32P
| 50 | 1401 | 2701-XZZSO-10101C | SDI0010-02R | 2701-X-10101C | - | 2701-XZZSO-10101C | Styrene Inlet Switch Valve of 2701-TK-1205S | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 08 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 17 | DI32
| 51 | 1401 | 2701-XZZSC-10101C | SDI0010-02R | 2701-X-10101C | - | 2701-XZZSC-10101C | Styrene Inlet Switch Valve of 2701-TK-1205S | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 03 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 16 | DI32
| 53 | 1401 | 2701-XZY-10102C | SDO0001-01 | 2701-X-10102C | 2701-Z-10001/2701-Z-10004/2701-Z-10103 | 2701-XZY-10102C | Styrene Inlet Switch Valve of 2701-TK-1205S | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 06 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 18 | DO32P
| 54 | 1401 | 2701-XZZSC-10102C | SDI0010-02R | 2701-X-10102C | 2701-Z-10103 | 2701-XZZSC-10102C | Styrene Inlet Switch Valve of 2701-TK-1205S | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 05 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 12 | DI32
| 56 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 04 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 3 | AI16H
| 57 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | - | 2701-LZIA-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 58 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | - | 2701-LZAHH-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 59 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | - | 2701-LZALL-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 61 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 02 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 9 | AI16H
| 62 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | - | 2701-LZIA-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 63 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | - | 2701-LZAHH-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 64 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | - | 2701-LZALL-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 66 | 1401 | 2701-XZY-10201A | SDO0001-01 | 2701-X-10201A | 2701-Z-10001/2701-Z-10004/2701-Z-10201 | 2701-XZY-10201A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10201 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 01 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 21 | DO32P
| 67 | 1401 | 2701-XZZSO-10201A | SDI0010-02R | 2701-X-10201A | - | 2701-XZZSO-10201A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update instrument type,location,IO type |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 06 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 24 | DI32
| 68 | 1401 | 2701-XZZSC-10201A | SDI0010-02R | 2701-X-10201A | - | 2701-XZZSC-10201A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update instrument type,location,IO type |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 14 | DI32
| 70 | 1401 | 2701-XZY-10202A | SDO0001-01 | 2701-X-10202A | 2701-Z-10001/2701-Z-10004/2701-Z-10202 | 2701-XZY-10202A | Dehydrogenation Mixture Outlet Switch Valve of 2701-TK-1204A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 03 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 16 | DO32P
| 71 | 1401 | 2701-XZZSC-10202A | SDI0010-02R | 2701-X-10202A | 2701-Z-10202 | 2701-XZZSC-10202A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update instrument type,location,IO type |  |  | Z-10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 12 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 9 | DI32
| 73 | 1401 | 2701-LZIA-10201B | SAI1000-01R | 2701-L-10201B | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10201B | Remote Liquid Level Gauge of 2701-TK-1204B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 05 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 4 | AI16H
| 74 | 1401 | 2701-LZIA-10201B | SAI1000-01R | 2701-L-10201B | - | 2701-LZIA-10201B | Remote Liquid Level Gauge of 2701-TK-1204B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 76 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 85,383 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 03 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 14 | AI16H
| 77 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | - | 2701-LZIA-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 78 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | - | 2701-LZAHH-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 79 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | - | 2701-LZALL-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 81 | 1401 | 2701-XZY-10201B | SDO0001-01 | 2701-X-10201B | 2701-Z-10001/2701-Z-10004/2701-Z-10201 | 2701-XZY-10201B | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10201 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 02 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 17 | DO32P
| 82 | 1401 | 2701-XZZSO-10201B | SDI0010-02R | 2701-X-10201B | - | 2701-XZZSO-10201B | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 07 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 19 | DI32
| 83 | 1401 | 2701-XZZSC-10201B | SDI0010-02R | 2701-X-10201B | - | 2701-XZZSC-10201B | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 02 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 15 | DI32
| 85 | 1401 | 2701-XZY-10202B | SDO0001-01 | 2701-X-10202B | 2701-Z-10001/2701-Z-10004/2701-Z-10202 | 2701-XZY-10202B | Dehydrogenation Mixture Outlet Switch Valve of 2701-TK-1204B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 04 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 19 | DO32P
| 86 | 1401 | 2701-XZZSC-10202B | SDI0010-02R | 2701-X-10202B | 2701-Z-10202 | 2701-XZZSC-10202B | Dehydrogenation Mixture Outlet Switch Valve of 2701-TK-1204B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 13 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 11 | DI32
| 88 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 06 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 5 | AI16H
| 89 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | - | 2701-LZIA-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 90 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | - | 2701-LZAH-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 91 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | - | 2701-LZAL-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 93 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 86,387 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 06 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 11 | AI16H
| 94 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | - | 2701-LZIA-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 95 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | - | 2701-LZAHH-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 96 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | - | 2701-LZALL-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 98 | 1401 | 2701-XZY-10301A | SDO0001-01 | 2701-X-10301A | 2701-Z-10001/2701-Z-10004/2701-Z-10301 | 2701-XZY-10301A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10301 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 05 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 22 | DO32P
| 99 | 1401 | 2701-XZZSO-10301A | SDI0010-02R | 2701-X-10301A | - | 2701-XZZSO-10301A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 08 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 20 | DI32
| 100 | 1401 | 2701-XZZSC-10301A | SDI0010-02R | 2701-X-10301A | - | 2701-XZZSC-10301A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 03 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 16 | DI32
| 102 | 1401 | 2701-XZY-10302A | SDO0001-01 | 2701-X-10302A | 2701-Z-10001/2701-Z-10004/2701-Z-10302 | 2701-XZY-10302A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 07 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 18 | DO32P
| 103 | 1401 | 2701-XZZSC-10302A | SDI0010-02R | 2701-X-10302A | 2701-Z-10302 | 2701-XZZSC-10302A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 11 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 22 | DI32
| 105 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 07 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 6 | AI16H
| 106 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | - | 2701-LZIA-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 107 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | - | 2701-LZAHH-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 108 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | - | 2701-LZALL-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 110 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 86,387 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 05 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 10 | AI16H
| 111 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | - | 2701-LZIA-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 112 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | - | 2701-LZAHH-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 113 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | - | 2701-LZALL-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 115 | 1401 | 2701-XZY-10301B | SDO0001-01 | 2701-X-10301B | 2701-Z-10001/2701-Z-10004/2701-Z-10301 | 2701-XZY-10301B | Ethylbenzene Inlet Switch Valve of 2701-TK-1202B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10301 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 06 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 20 | DO32P
| 116 | 1401 | 2701-XZZSO-10301B | SDI0010-02R | 2701-X-10301B | - | 2701-XZZSO-10301B | Ethylbenzene Inlet Switch Valve of 2701-TK-1202B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 09 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 25 | DI32
| 117 | 1401 | 2701-XZZSC-10301B | SDI0010-02R | 2701-X-10301B | - | 2701-XZZSC-10301B | Ethylbenzene Inlet Switch Valve of 2701-TK-1202B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 04 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 17 | DI32
| 119 | 1401 | 2701-XZY-10302B | SDO0001-01 | 2701-X-10302B | 2701-Z-10001/2701-Z-10004/2701-Z-10302 | 2701-XZY-10302B | Ethylbenzene Outlet Switch Valve of 2701-TK-1202B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 08 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 15 | DO32P
| 120 | 1401 | 2701-XZZSC-10302B | SDI0010-02R | 2701-X-10302B | 2701-Z-10302 | 2701-XZZSC-10302B | Ethylbenzene Outlet Switch Valve of 2701-TK-1202B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 12 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 23 | DI32
| 122 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | 2701-Z-10401/2701-Z-10402 | 2701-LZT-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10401/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 08 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 7 | AI16H
| 123 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | - | 2701-LZIA-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 124 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | - | 2701-LZAHH-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 125 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | - | 2701-LZALL-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 127 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | 2701-Z-10401/2701-Z-10402 | 2701-LZT-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 86,24 | kPa | 400 | 10400 | mm | - | - | - | - | - | 0 | - |  |  | Z-10401/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 04 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 12 | AI16H
| 128 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | - | 2701-LZIA-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 129 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | - | 2701-LZAHH-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 130 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | - | 2701-LZALL-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 132 | 1401 | 2701-XZY-10401 | SDO0001-01 | 2701-X-10401 | 2701-Z-10001/2701-Z-10004/2701-Z-10401 | 2701-XZY-10401 | Benzene Inlet Switch Valve of 2701-TK-1201 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10401 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 09 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 23 | DO32P
| 133 | 1401 | 2701-XZZSO-10401 | SDI0010-02R | 2701-X-10401 | - | 2701-XZZSO-10401 | Benzene Inlet Switch Valve of 2701-TK-1201 | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 10 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 21 | DI32
| 134 | 1401 | 2701-XZZSC-10401 | SDI0010-02R | 2701-X-10401 | - | 2701-XZZSC-10401 | Benzene Inlet Switch Valve of 2701-TK-1201 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 05 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 18 | DI32
| 136 | 1401 | 2701-XZY-10402 | SDO0001-01 | 2701-X-10402 | 2701-Z-10001/2701-Z-10004/2701-Z-10402 | 2701-XZY-10402 | Benzene Outlet Switch Valve of 2701-TK-1201 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 07 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 19 | DO32P
| 137 | 1401 | 2701-XZZSC-10402 | SDI0010-02R | 2701-X-10402 | - | 2701-XZZSC-10402 | Benzene Outlet Switch Valve of 2701-TK-1201 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 14 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 4 | DI32
| 139 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | 2701-Z-10501/2701-Z-10502 | 2701-LZT-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 11500 | mm | 0 | 11500 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10501/10502 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 09 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 8 | AI16H
| 140 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | - | 2701-LZIA-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | 0 | 11500 | mm | 0 | 11500 | mm | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 141 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | - | 2701-LZAHH-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 142 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | - | 2701-LZALL-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 144 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | 2701-Z-10501/2701-Z-10502 | 2701-LZT-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 93,551 | kPa | 400 | 11500 | mm | - | - | - | - | - | 0 | - |  |  | Z-10501/10502 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 07 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 1 | AI16H
| 145 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | - | 2701-LZIA-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 146 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | - | 2701-LZAHH-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 147 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | - | 2701-LZALL-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 149 | 1401 | 2701-XZY-10501 | SDO0001-01 | 2701-X-10501 | 2701-Z-10002/2701-Z-10004/2701-Z-10501 | 2701-XZY-10501 | Off-Spec Ethylbenzene Inlet Switch Valve of 2701-TK-1203 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10501 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 02 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 3 | DO32P
| 150 | 1401 | 2701-XZZSO-10501 | SDI0010-02R | 2701-X-10501 | - | 2701-XZZSO-10501 | Off-Spec Ethylbenzene Inlet Switch Valve of 2701-TK-1203 | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 06 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 2 | DI32
| 151 | 1401 | 2701-XZZSC-10501 | SDI0010-02R | 2701-X-10501 | - | 2701-XZZSC-10501 | Off-Spec Ethylbenzene Inlet Switch Valve of 2701-TK-1203 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 14 | DI32
| 153 | 1401 | 2701-XZY-10502 | SDO0001-01 | 2701-X-10502 | 2701-Z-10002/2701-Z-10004/2701-Z-10502 | 2701-XZY-10502 | Off-Spec Ethylbenzene Outlet Switch Valve of 2701-TK-1203 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10502 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 03 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 10 | DO32P
| 154 | 1401 | 2701-XZZSC-10502 | SDI0010-02R | 2701-X-10502 | - | 2701-XZZSC-10502 | Off-Spec Ethylbenzene Outlet Switch Valve of 2701-TK-1203 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 03 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 6 | DI32
Изм 2026.06.19 Change io type DIR-VFC -> S | 156 | 1401 | 2701-HZS-10003 | SDO0001-01 | 2701-HZS-10003 | 2701-Z-10002 | 2701-HZS-10003 | Fire dike isolation interlock 2 | Soft Push button | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change to soft button |  |  | Z-10002 | B3 NKNH21002-1401-ATX.LST-0004_4_EN
| 157 | 1401 | 2701-HZS-10004 | SDI0010-01R | 2701-HZS-10004 | 2701-Z-10002 | 2701-HZS-10004 | Manual confirmation | PUSH BUTTON | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B042/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2701-S-JB-B042 | SIS |  | BK | 02 | Rev3 JB No. Change | 1401 |  |  | 2701-S-JB-B042 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 2 | DI32
| 159 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 8250 | mm | 0 | 8250 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 10 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 9 | AI16H
| 160 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | - | 2701-LZIA-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 161 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | - | 2701-LZAHH-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 162 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | - | 2701-LZALL-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 164 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 62,916 | kPa | 400 | 7900 | mm | - | - | - | - | - | 0 | - |  |  | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 05 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 5 | AI16H
| 165 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | - | 2701-LZIA-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 166 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | - | 2701-LZAHH-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 167 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | - | 2701-LZALL-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 169 | 1401 | 2701-XZY-10601A | SDO0001-01 | 2701-X-10601A | 2701-Z-10002/2701-Z-10004/2701-Z-10601 | 2701-XZY-10601A | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10601 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 04 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 4 | DO32P
| 170 | 1401 | 2701-XZZSO-10601A | SDI0010-02R | 2701-X-10601A | - | 2701-XZZSO-10601A | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 07 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 3 | DI32
| 171 | 1401 | 2701-XZZSC-10601A | SDI0010-02R | 2701-X-10601A | - | 2701-XZZSC-10601A | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 02 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 4 | DI32
| 173 | 1401 | 2701-XZY-10602A | SDO0001-01 | 2701-X-10602A | 2701-Z-10002/2701-Z-10004/2701-Z-10602 | 2701-XZY-10602A | Benzene/Toluene Mixture Outlet Switch Valve of 2701-TK-1206A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 06 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 5 | DO32P
| 174 | 1401 | 2701-XZZSC-10602A | SDI0010-02R | 2701-X-10602A | 2701-Z-10602 | 2701-XZZSC-10602A | Benzene/Toluene Mixture Outlet Switch Valve of 2701-TK-1206A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 04 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 1 | DI32
| 176 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 8250 | mm | 0 | 8250 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 11 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 10 | AI16H
| 177 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | - | 2701-LZIA-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 178 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | - | 2701-LZAHH-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 179 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | - | 2701-LZALL-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 181 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 62,916 | kPa | 400 | 7900 | mm | - | - | - | - | - | 0 | - |  |  | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 06 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 2 | AI16H
| 182 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | - | 2701-LZIA-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 183 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | - | 2701-LZAHH-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 184 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | - | 2701-LZALL-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 186 | 1401 | 2701-XZY-10601B | SDO0001-01 | 2701-X-10601B | 2701-Z-10002/2701-Z-10004/2701-Z-10601 | 2701-XZY-10601B | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10601 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 05 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 6 | DO32P
| 187 | 1401 | 2701-XZZSO-10601B | SDI0010-02R | 2701-X-10601B | - | 2701-XZZSO-10601B | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 08 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 5 | DI32
| 188 | 1401 | 2701-XZZSC-10601B | SDI0010-02R | 2701-X-10601B | - | 2701-XZZSC-10601B | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 03 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 6 | DI32
| 190 | 1401 | 2701-XZY-10602B | SDO0001-01 | 2701-X-10602B | 2701-Z-10002/2701-Z-10004/2701-Z-10602 | 2701-XZY-10602B | Benzene/Toluene Mixture Outlet Switch Valve of 2701-TK-1206B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 07 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 7 | DO32P
| 191 | 1401 | 2701-XZZSC-10602B | SDI0010-02R | 2701-X-10602B | 2701-Z-10602 | 2701-XZZSC-10602B | Benzene/Toluene Mixture Outlet Switch Valve of 2701-TK-1206B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 05 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 3 | DI32
| 193 | 1401 | 2701-LZIA-10701A | SAI1000-01R | 2701-L-10701A | 2701-Z-10701/2701-Z-10702 | 2701-LZT-10701A | Remote Liquid Level Gauge of 2701-TK-1207A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 9600 | mm | 0 | 9600 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10701/10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 12 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 11 | AI16H
| 194 | 1401 | 2701-LZIA-10701A | SAI1000-01R | 2701-L-10701A | - | 2701-LZIA-10701A | Remote Liquid Level Gauge of 2701-TK-1207A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 195 | 1401 | 2701-LZIA-10701A | SAI1000-01R | 2701-L-10701A | - | 2701-LZAHH-10701A | Remote Liquid Level Gauge of 2701-TK-1207A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 196 | 1401 | 2701-LZIA-10701A | SAI1000-01R | 2701-L-10701A | - | 2701-LZALL-10701A | Remote Liquid Level Gauge of 2701-TK-1207A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 198 | 1401 | 2701-LZIA-10702A | SAI1000-01R | 2701-L-10702A | 2701-Z-10701/2701-Z-10702 | 2701-LZT-10702A | Remote Liquid Level Gauge of 2701-TK-1207A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 81,928 | kPa | 400 | 9200 | mm | - | - | - | - | - | 0 | - |  |  | Z-10701/10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 02 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 3 | AI16H
| 199 | 1401 | 2701-LZIA-10702A | SAI1000-01R | 2701-L-10702A | - | 2701-LZIA-10702A | Remote Liquid Level Gauge of 2701-TK-1207A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 200 | 1401 | 2701-LZIA-10702A | SAI1000-01R | 2701-L-10702A | - | 2701-LZAHH-10702A | Remote Liquid Level Gauge of 2701-TK-1207A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 201 | 1401 | 2701-LZIA-10702A | SAI1000-01R | 2701-L-10702A | - | 2701-LZALL-10702A | Remote Liquid Level Gauge of 2701-TK-1207A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 203 | 1401 | 2701-XZY-10701A | SDO0001-01 | 2701-X-10701A | 2701-Z-10003/2701-Z-10004/2701-Z-10701 | 2701-XZY-10701A | Heavy Tar Inlet Switch Valve of 2701-TK-1207A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10003/10004/10701 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 08 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 8 | DO32P
| 204 | 1401 | 2701-XZZSO-10701A | SDI0010-02R | 2701-X-10701A | - | 2701-XZZSO-10701A | Heavy Tar Inlet Switch Valve of 2701-TK-1207A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 09 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 8 | DI32
| 205 | 1401 | 2701-XZZSC-10701A | SDI0010-02R | 2701-X-10701A | - | 2701-XZZSC-10701A | Heavy Tar Inlet Switch Valve of 2701-TK-1207A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 04 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 10 | DI32
| 207 | 1401 | 2701-XZY-10702A | SDO0001-01 | 2701-X-10702A | 2701-Z-10003/2701-Z-10004/2701-Z-10702 | 2701-XZY-10702A | Heavy Tar Outlet Switch Valve of 2701-TK-1207A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10003/10004/10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 10 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 9 | DO32P
| 208 | 1401 | 2701-XZZSC-10702A | SDI0010-02R | 2701-X-10702A | 2701-Z-10702 | 2701-XZZSC-10702A | Heavy Tar Outlet Switch Valve of 2701-TK-1207A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 06 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 5 | DI32
Изм 2026.06.19 Change io type DIR-VFC -> S | 210 | 1401 | 2701-HZS-10005 | SDO0001-01 | 2701-HZS-10005 | 2701-Z-10003 | 2701-HZS-10005 | Fire dike isolation interlock 3 | Soft Push button | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change to soft button |  |  | Z-10003 | B3 NKNH21002-1401-ATX.LST-0004_4_EN
| 211 | 1401 | 2701-HZS-10006 | SDI0010-01R | 2701-HZS-10006 | 2701-Z-10003 | 2701-HZS-10006 | Manual confirmation | PUSH BUTTON | 2000-S-SC-B01 | 2490156-1401-PR007-0107A | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10003 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B042/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2701-S-JB-B042 | SIS |  | BK | 03 | Rev3 JB No. Change | 1401 |  |  | 2701-S-JB-B042 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 0 | DI32
| 213 | 1401 | 2701-LZIA-10701B | SAI1000-01R | 2701-L-10701B | 2701-Z-10701/2701-Z-10702 | 2701-LZT-10701B | Remote Liquid Level Gauge of 2701-TK-1207B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 9600 | mm | 0 | 9600 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10701/10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 13 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 12 | AI16H
| 214 | 1401 | 2701-LZIA-10701B | SAI1000-01R | 2701-L-10701B | - | 2701-LZIA-10701B | Remote Liquid Level Gauge of 2701-TK-1207B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 215 | 1401 | 2701-LZIA-10701B | SAI1000-01R | 2701-L-10701B | - | 2701-LZAHH-10701B | Remote Liquid Level Gauge of 2701-TK-1207B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 216 | 1401 | 2701-LZIA-10701B | SAI1000-01R | 2701-L-10701B | - | 2701-LZALL-10701B | Remote Liquid Level Gauge of 2701-TK-1207B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 218 | 1401 | 2701-LZIA-10702B | SAI1000-01R | 2701-L-10702B | 2701-Z-10701/2701-Z-10702 | 2701-LZT-10702B | Remote Liquid Level Gauge of 2701-TK-1207B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 81,928 | kPa | 400 | 9200 | mm | - | - | - | - | - | 0 | - |  |  | Z-10701/10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 04 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 6 | AI16H
| 219 | 1401 | 2701-LZIA-10702B | SAI1000-01R | 2701-L-10702B | - | 2701-LZIA-10702B | Remote Liquid Level Gauge of 2701-TK-1207B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 220 | 1401 | 2701-LZIA-10702B | SAI1000-01R | 2701-L-10702B | - | 2701-LZAHH-10702B | Remote Liquid Level Gauge of 2701-TK-1207B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 221 | 1401 | 2701-LZIA-10702B | SAI1000-01R | 2701-L-10702B | - | 2701-LZALL-10702B | Remote Liquid Level Gauge of 2701-TK-1207B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 223 | 1401 | 2701-XZY-10701B | SDO0001-01 | 2701-X-10701B | 2701-Z-10003/2701-Z-10004/2701-Z-10701 | 2701-XZY-10701B | Heavy Tar Inlet Switch Valve of 2701-TK-1207B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10003/10004/10701 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 09 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 11 | DO32P
| 224 | 1401 | 2701-XZZSO-10701B | SDI0010-02R | 2701-X-10701B | - | 2701-XZZSO-10701B | Heavy Tar Inlet Switch Valve of 2701-TK-1207B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 10 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 13 | DI32
| 225 | 1401 | 2701-XZZSC-10701B | SDI0010-02R | 2701-X-10701B | - | 2701-XZZSC-10701B | Heavy Tar Inlet Switch Valve of 2701-TK-1207B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 05 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 15 | DI32
| 227 | 1401 | 2701-XZY-10702B | SDO0001-01 | 2701-X-10702B | 2701-Z-10003/2701-Z-10004/2701-Z-10702 | 2701-XZY-10702B | Heavy Tar Outlet Switch Valve of 2701-TK-1207B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10003/10004/10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 11 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 14 | DO32P
| 228 | 1401 | 2701-XZZSC-10702B | SDI0010-02R | 2701-X-10702B | 2701-Z-10702 | 2701-XZZSC-10702B | Heavy Tar Outlet Switch Valve of 2701-TK-1207B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0107B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10702 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 07 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 12 | DI32
| 230 | 1401 | 2701-LZIA-10801 | SAI1000-01R | 2701-L-10801 | 2701-Z-10801 | 2701-LZT-10801 | Remote Liquid Level Gauge of 2701-V-1701 | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0108 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 17,444 | kPa | 0 | 2000 | mm | - | - | - | - | - | 0 | - |  |  | Z-10801 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 03 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 7 | AI16H
| 231 | 1401 | 2701-LZIA-10801 | SAI1000-01R | 2701-L-10801 | - | 2701-LZIA-10801 | Remote Liquid Level Gauge of 2701-V-1701 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0108 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 232 | 1401 | 2701-LZIA-10801 | SAI1000-01R | 2701-L-10801 | - | 2701-LZALL-10801 | Remote Liquid Level Gauge of 2701-V-1701 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0108 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 234 | 1401 | 2701-AZIA-11001A | SAI1000-01R | 2701-A-11001A | 2701-Z-11001 | 2701-AZT-11001A | Oxygen content analysis of Off-gas mains | LASER OXYGEN ANALYZER | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | AIR-E | Ex.d | SIS | - | I | 0 | 5 | %VOL | 0 | 5 | %VOL | - | - | - | - | - | 1 | Rev1 add signal isolator |  |  | Z-11001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-AZT-11001A/SIS | 1x2x1.5mm2,PE-OS-PE-LSZH,Fire Resistant | NH-DJYVP3 1x2x1.5 | 2701-AZT-11001A | SIS |  | BK | 01 | Rev1 New add | 1401 |  |  | SIS |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 11 | AI16H
| 235 | 1401 | 2701-AZIA-11001A | SAI1000-01R | 2701-A-11001A | - | 2701-AZIA-11001A | Oxygen content analysis of Off-gas mains | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 236 | 1401 | 2701-AZIA-11001A | SAI1000-01R | 2701-A-11001A | - | 2701-AZAH-11001A | Oxygen content analysis of Off-gas mains | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 237 | 1401 | 2701-AZIA-11001A | SAI1000-01R | 2701-A-11001A | - | 2701-AZAHH-11001A | Oxygen content analysis of Off-gas mains | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 239 | 1401 | 2701-AZIA-11001B | SAI1000-01R | 2701-A-11001B | 2701-Z-11001 | 2701-AZT-11001B | Oxygen content analysis of Off-gas mains | LASER OXYGEN ANALYZER | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | AIR-E | Ex.d | SIS | - | I | 0 | 5 | %VOL | 0 | 5 | %VOL | - | - | - | - | - | 1 | Rev1 add signal isolator |  |  | Z-11001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-AZT-11001B/SIS | 1x2x1.5mm2,PE-OS-PE-LSZH,Fire Resistant | NH-DJYVP3 1x2x1.5 | 2701-AZT-11001B | SIS |  | BK | 01 | Rev1 New add | 1401 |  |  | SIS |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 12 | AI16H
| 240 | 1401 | 2701-AZIA-11001B | SAI1000-01R | 2701-A-11001B | - | 2701-AZIA-11001B | Oxygen content analysis of Off-gas mains | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 241 | 1401 | 2701-AZIA-11001B | SAI1000-01R | 2701-A-11001B | - | 2701-AZAH-11001B | Oxygen content analysis of Off-gas mains | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 242 | 1401 | 2701-AZIA-11001B | SAI1000-01R | 2701-A-11001B | - | 2701-AZAHH-11001B | Oxygen content analysis of Off-gas mains | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 244 | 1401 | 2701-AZIA-11001C | SAI1000-01R | 2701-A-11001C | 2701-Z-11001 | 2701-AZT-11001C | Oxygen content analysis of Off-gas mains | LASER OXYGEN ANALYZER | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | AIR-E | Ex.d | SIS | - | I | 0 | 5 | %VOL | 0 | 5 | %VOL | - | - | - | - | - | 1 | Rev1 add signal isolator |  |  | Z-11001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-AZT-11001C/SIS | 1x2x1.5mm2,PE-OS-PE-LSZH,Fire Resistant | NH-DJYVP3 1x2x1.5 | 2701-AZT-11001C | SIS |  | BK | 01 | Rev1 New add | 1401 |  |  | SIS |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 13 | AI16H
| 245 | 1401 | 2701-AZIA-11001C | SAI1000-01R | 2701-A-11001C | - | 2701-AZIA-11001C | Oxygen content analysis of Off-gas mains | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 246 | 1401 | 2701-AZIA-11001C | SAI1000-01R | 2701-A-11001C | - | 2701-AZAH-11001C | Oxygen content analysis of Off-gas mains | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 247 | 1401 | 2701-AZIA-11001C | SAI1000-01R | 2701-A-11001C | - | 2701-AZAHH-11001C | Oxygen content analysis of Off-gas mains | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 249 | 1401 | 2701-XZY-11001 | SDO0001-01 | 2701-X-11001 | 2701-Z-11001 | 2701-XZY-11001 | Off-gas Outlet Switch Valve of OG-11002 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-11001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 12 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 12 | DO32P
| 250 | 1401 | 2701-XZZSO-11001 | SDI0010-02R | 2701-X-11001 | - | 2701-XZZSO-11001 | Off-gas Outlet Switch Valve of OG-11002 | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 13 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 0 | DI32
| 251 | 1401 | 2701-XZZSC-11001 | SDI0010-02R | 2701-X-11001 | - | 2701-XZZSC-11001 | Off-gas Outlet Switch Valve of OG-11002 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 08 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 10 | DI32
| 253 | 1401 | 2602-XZY-11002 | SDO0001-01 | 2602-X-11002 | 2701-Z-11002 | 2602-XZY-11002 | Nitrogen Medium Pressure Intlet Switch Valve | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-11002 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 01 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 13 | DO32P
| 254 | 1401 | 2602-XZZSO-11002 | SDI0010-02R | 2602-X-11002 | - | 2602-XZZSO-11002 | Nitrogen Medium Pressure Intlet Switch Valve | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 02 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 2 | DI32
| 255 | 1401 | 2602-XZZSC-11002 | SDI0010-02R | 2602-X-11002 | - | 2602-XZZSC-11002 | Nitrogen Medium Pressure Intlet Switch Valve | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 8 | DI32
| 257 | 1401 | 2603-XZY-11301 | SDO0001-01 | 2603-X-11301 | 2701-Z-10004/2701-Z-11301 | 2603-XZY-11301 | Fuel gas Iutlet Switch Valve | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0111A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 Change PBS. of Tag No. Rev1 New add |  |  | Z-10004/11301 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 10 |  | 1401 |  |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 5 | DO32P
| 258 | 1401 | 2603-XZZSO-11301 | SDI0010-02R | 2603-X-11301 | - | 2603-XZZSO-11301 | Fuel gas Iutlet Switch Valve | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0111A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 Change PBS. of Tag No. Rev1 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 13 |  | 1401 |  |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 11 | DI32
| 259 | 1401 | 2603-XZZSC-11301 | SDI0010-02R | 2603-X-11301 | - | 2603-XZZSC-11301 | Fuel gas Iutlet Switch Valve | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0111A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 Change PBS. of Tag No. Rev1 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 14 |  | 1401 |  |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 7 | DI32
| 261 | 1401 | 2603-XZY-11302 | SDO0001-01 | 2603-X-11302 | 2701-Z-10004/2701-Z-11301 | 2603-XZY-11302 | Fuel gas Outlet Switch Valve | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0111C | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 Change PBS. of Tag No. Rev1 New add |  |  | Z-10004/11301 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 11 |  | 1401 |  |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 6 | DO32P
| 262 | 1401 | 2603-XZZSO-11302 | SDI0010-02R | 2603-X-11302 | - | 2603-XZZSO-11302 | Fuel gas Outlet Switch Valve | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0111C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 Change PBS. of Tag No. Rev1 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 14 |  | 1401 |  |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 14 | DI32
| 263 | 1401 | 2603-XZZSC-11302 | SDI0010-02R | 2603-X-11302 | - | 2603-XZZSC-11302 | Fuel gas Outlet Switch Valve | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0111C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 Change PBS. of Tag No. Rev1 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 15 |  | 1401 |  |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 13 | DI32
| 265 | 1401 | 2603-FZIA-11001 | SAI1000-01R | 2603-F-11001 | 2701-Z-11002 | 2603-FZT-11001 | Fuel Gas Flow Meter | Integral Orifice | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 25 | kPa | 0 | 15 | Nm3/h | - | - | - | - | - | 0 | - |  |  | Z-11002 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 4 | AI16H
| 266 | 1401 | 2603-FZIA-11001 | SAI1000-01R | 2603-F-11001 | - | 2603-FZIA-11001 | Fuel Gas Flow Meter | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 267 | 1401 | 2603-FZIA-11001 | SAI1000-01R | 2603-F-11001 | - | 2603-FZAL-11001 | Fuel Gas Flow Meter | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 268 | 1401 | 2603-FZIA-11001 | SAI1000-01R | 2603-F-11001 | - | 2603-FZALL-11001 | Fuel Gas Flow Meter | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0110 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 270 | 1401 | 2701-TZIA-10761A | SAI1000-01R | 2701-T-10761A | 2701-Z-10705 | 2701-TZT-10761A | Temperature Transmitter For Pump Bearing 2701-P-1207A | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Tag change | 2701-P-1207A | SDPump | Z-10705 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C103/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C103 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C103 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 6 | AI16H
| 271 | 1401 | 2701-PZIA-10761A | SAI1000-01R | 2701-P-10761A | 2701-Z-10705 | 2701-PZT-10761A | Pressure Transmitter on Accumulator 2701-P-1207A | PRESSURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 2,5 | MPag | 0 | 1,6 | MPag | 0,4 | 0,45 | - | - | Mpag | 4 | Rev4 change system range Rev1 Tag change | 2701-P-1207A | SDPump | Z-10705 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C103/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C103 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C103 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 7 | AI16H
| 272 | 1401 | 2701-TZIA-10761B | SAI1000-01R | 2701-T-10761B | 2701-Z-10705 | 2701-TZT-10761B | Temperature Transmitter For Pump Bearing 2701-P-1207B | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Tag change | 2701-P-1207B | SDPump | Z-10705 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C104/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C104 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C104 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 8 | AI16H
| 273 | 1401 | 2701-PZIA-10761B | SAI1000-01R | 2701-P-10761B | 2701-Z-10705 | 2701-PZT-10761B | Pressure Transmitter on Accumulator 2701-P-1207B | PRESSURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 2,5 | MPag | 0 | 1,6 | MPag | 0,4 | 0,45 | - | - | Mpag | 4 | Rev4 change system range Rev1 Tag change | 2701-P-1207B | SDPump | Z-10705 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C104/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C104 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C104 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 9 | AI16H
| 274 | 1401 | 2701-PZIA-10961 | SAI1000-01R | 2701-P-10961 | 2701-Z-10903 | 2701-PZT-10961 | Seal auxiliary system of 2701-P-1215 | PRESSURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 0,3 | Mpag | - | - | - | - | - | 0,1 | - | Mpag | 1 | Rev1 Tag change | 2701-P-1215 | VINCI | Z-10903 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C101/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C101 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C101 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 2 | AI16H
| 275 | 1401 | 2701-LZIA-10961 | SAI1000-01R | 2701-L-10961 | 2701-Z-10903 | 2701-LZT-10961 | Seal auxiliary system of 2701-P-1215 | LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | - | - | - | 0 | 400 | mmH2O | - | 85 | 302 | - | mmH2O | 1 | Rev1 Tag change | 2701-P-1215 | VINCI | Z-10903 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C101/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C101 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C101 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 0 | AI16H
| 276 | 1401 | 2701-TZIA-10961 | SAI1000-01R | 2701-T-10961 | 2701-Z-10903 | 2701-TZT-10961 | Bearing temperature of 2701-P-1215 | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | - | - | - | - | - | 85 | - | ℃ | 3 | Rev3 Change instrument range Rev2 Change service Rev1 Tag change | 2701-P-1215 | VINCI | Z-10903 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C101/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C101 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C101 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 1 | AI16H
| 277 | 1401 | 2701-PZIA-10962 | SAI1000-01R | 2701-P-10962 | 2701-Z-10904 | 2701-PZT-10962 | Seal auxiliary system of 2701-P-1216 | PRESSURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 0,3 | Mpag | - | - | - | - | - | 0,1 | - | Mpag | 1 | Rev1 Tag change | 2701-P-1216 | VINCI | Z-10904 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C102/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C102 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C102 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 3 | AI16H
| 278 | 1401 | 2701-LZIA-10962 | SAI1000-01R | 2701-L-10962 | 2701-Z-10904 | 2701-LZT-10962 | Seal auxiliary system of 2701-P-1216 | LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | - | - | - | 0 | 400 | mmH2O | - | 85 | 302 | - | mmH2O | 1 | Rev1 Tag change | 2701-P-1216 | VINCI | Z-10904 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C102/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C102 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C102 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 4 | AI16H
| 279 | 1401 | 2701-TZIA-10962 | SAI1000-01R | 2701-T-10962 | 2701-Z-10904 | 2701-TZT-10962 | Bearing temperature of 2701-P-1216 | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0000C | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | - | - | - | - | - | 85 | - | ℃ | 3 | Rev3 Change instrument range Rev2 Change service Rev1 Tag change | 2701-P-1216 | VINCI | Z-10904 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C102/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2701-S-JB-C102 | SIS |  | BU |  | Rev1 new add for package | 1401 |  |  | 2701-S-JB-C102 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 5 | AI16H
| 280 | 1401 | 2604-PZIA-11402A | SAI1000-01R | 2604-P-11402A | 2604-Z-10005 | 2604-PZT-11402A | Pressure indicate of IA system | PRESSURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0114 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 1 | Mpag | - | - | - | 0,38 | 0,4 | - | - | Mpag | 4 | Rev4 New add | 2701-P-1216 | VINCI | Z-10904 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 11 | AI16H
| 281 | 1401 | 2604-PZIA-11402B | SAI1000-01R | 2604-P-11402B | 2604-Z-10005 | 2604-PZT-11402B | Pressure indicate of IA system | PRESSURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0114 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 1 | Mpag | - | - | - | 0,38 | 0,4 | - | - | Mpag | 4 | Rev4 New add | 2701-P-1216 | VINCI | Z-10904 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 12 | AI16H
| 282 | 1401 | 2604-PZIA-11402C | SAI1000-01R | 2604-P-11402C | 2604-Z-10005 | 2604-PZT-11402C | Pressure indicate of IA system | PRESSURE TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0114 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 1 | Mpag | - | - | - | 0,38 | 0,4 | - | - | Mpag | 4 | Rev4 New add | 2701-P-1216 | VINCI | Z-10904 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 13 | AI16H
| 284 | 1401 | 2701-MXI-01205A | SDO0001-01 | 2701-MXI-01205A | 2701-Z-10001/2701-Z-10004/2701-Z-10102/2701-Z-10103 | 2701-MXI-01205A | SM Transfer Pump 2701-P-1205A Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0101D | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10102/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 0 | DO32P
| 285 | 1401 | 2701-MXI-11205A | SDO0001-01 | 2701-MXI-11205A | 2701-Z-10001/2701-Z-10004/2701-Z-10102/2701-Z-10103 | 2701-MXI-11205A | SM Transfer Pump 2701-P-1205B Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0101D | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10102/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 1 | DO32P
| 286 | 1401 | 2701-MXI-21205A | SDO0001-01 | 2701-MXI-21205A | 2701-Z-10001/2701-Z-10004/2701-Z-10102/2701-Z-10103 | 2701-MXI-21205A | SM Transfer Pump 2701-P-1205S Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0101D | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10102/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 2 | DO32P
| 287 | 1401 | 2701-MXI-01204A | SDO0001-01 | 2701-MXI-01204A | 2701-Z-10001/2701-Z-10004/2701-Z-10202 | 2701-MXI-01204A | DM Transfer Pump 2701-P-1204A Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0102B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 3 | DO32P
| 288 | 1401 | 2701-MXI-11204A | SDO0001-01 | 2701-MXI-11204A | 2701-Z-10001/2701-Z-10004/2701-Z-10202 | 2701-MXI-11204A | DM Transfer Pump 2701-P-1204B Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0102B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 4 | DO32P
| 289 | 1401 | 2701-MXI-01202A | SDO0001-01 | 2701-MXI-01202A | 2701-Z-10001/2701-Z-10004/2701-Z-10302 | 2701-MXI-01202A | EB Transfer Pump 2701-P-1202A Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0103B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 5 | DO32P
| 290 | 1401 | 2701-MXI-11202A | SDO0001-01 | 2701-MXI-11202A | 2701-Z-10001/2701-Z-10004/2701-Z-10302 | 2701-MXI-11202A | EB Transfer Pump 2701-P-1202B Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0103B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 6 | DO32P
| 291 | 1401 | 2701-MXI-01201A | SDO0001-01 | 2701-MXI-01201A | 2701-Z-10001/2701-Z-10004/2701-Z-10402 | 2701-MXI-01201A | Benzene Transfer Pump 2701-P-1201A Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0104 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 7 | DO32P
| 292 | 1401 | 2701-MXI-11201A | SDO0001-01 | 2701-MXI-11201A | 2701-Z-10001/2701-Z-10004/2701-Z-10402 | 2701-MXI-11201A | Benzene Transfer Pump 2701-P-1201B Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0104 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 8 | DO32P
| 293 | 1401 | 2701-MXI-01203A | SDO0001-01 | 2701-MXI-01203A | 2701-Z-10002/2701-Z-10004/2701-Z-10502 | 2701-MXI-01203A | Off-Spec EB Transfer Pump 2701-P-1203 Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0105 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10502 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 9 | DO32P
| 294 | 1401 | 2701-MXI-01206A | SDO0001-01 | 2701-MXI-01206A | 2701-Z-10002/2701-Z-10004/2701-Z-10602 | 2701-MXI-01206A | Benzene-Toluene Fraction Pump 2701-P-1206A Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0106B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 10 | DO32P
| 295 | 1401 | 2701-MXI-11206A | SDO0001-01 | 2701-MXI-11206A | 2701-Z-10002/2701-Z-10004/2701-Z-10602 | 2701-MXI-11206A | Benzene-Toluene Fraction Pump 2701-P-1206B Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0106B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 11 | DO32P
| 296 | 1401 | 2701-MXI-01207A | SDO0001-01 | 2701-MXI-01207A | 2701-Z-10003/2701-Z-10004/2701-Z-10702/2701-Z-10705 | 2701-MXI-01207A | Heavy tar Loading Pump 2701-P-1207A Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0107B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10003/10004/10702/10705 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 12 | DO32P
| 297 | 1401 | 2701-MXI-11207A | SDO0001-01 | 2701-MXI-11207A | 2701-Z-10003/2701-Z-10004/2701-Z-10702/2701-Z-10705 | 2701-MXI-11207A | Heavy tar Loading Pump 2701-P-1207B Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0107B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10003/10004/10702/10705 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 13 | DO32P
| 298 | 1401 | 2701-MXI-01701A | SDO0001-01 | 2701-MXI-01701A | 2701-Z-10004/2701-Z-10801 | 2701-MXI-01701A | TBC Solution Dosing Pump 2701-P-1701A Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0108 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10004/10801 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 14 | DO32P
| 299 | 1401 | 2701-MXI-11701A | SDO0001-01 | 2701-MXI-11701A | 2701-Z-10004/2701-Z-10801 | 2701-MXI-11701A | TBC Solution Dosing Pump 2701-P-1701B Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0108 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10004/10801 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 15 | DO32P
| 300 | 1401 | 2701-MXI-01215A | SDO0001-01 | 2701-MXI-01215A | 2701-Z-10903 | 2701-MXI-01215A | Stop Drum HC Pump 2701-P-1215 Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0000C | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10903 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 16 | DO32P
| 301 | 1401 | 2701-MXI-01216A | SDO0001-01 | 2701-MXI-01216A | 2701-Z-10904 | 2701-MXI-01216A | Stop Drum Water Pump 2701-P-1216 Stop | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0000C | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10904 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 17 | DO32P
| 302 | 1401 | 2701-MXI-21201A | SDO0001-01 | 2701-MXI-21201A | 2701-Z-10004/2701-Z-11001 | 2701-MXI-21201A | Exhaust gas Fan 2701-PK-1201A | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0110 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004/11001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 18 | DO32P
| 303 | 1401 | 2701-MXI-31201A | SDO0001-01 | 2701-MXI-31201A | 2701-Z-10004/2701-Z-11001 | 2701-MXI-31201A | Exhaust gas Fan 2701-PK-1201B | Relay Contact(230VAC) | 2202-S-RC-S07 | 2490156-1401-PR007-0110 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004/11001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [14 empty] | 2202 | 2202-S-RC-S07 | 2202-S-RC-S07 |  | A80 | A81 | 02 | 03 | A80-02 | A80-03 | A81-02 | A81-03 | 19 | DO32P
| 305 | 1401 | 2701-GZY-10004A | SDI0010-01R | 2701-GZY-10004A | - | 2701-GZY-10004A | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004A | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 9 | DI32
| 306 | 1401 | 2701-GZY-10004B | SDI0010-01R | 2701-GZY-10004B | - | 2701-GZY-10004B | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004B | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 10 | DI32
| 307 | 1401 | 2701-GZY-10004C | SDI0010-01R | 2701-GZY-10004C | - | 2701-GZY-10004C | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004C | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 11 | DI32
| 308 | 1401 | 2701-GZY-10004D | SDI0010-01R | 2701-GZY-10004D | - | 2701-GZY-10004D | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004D | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 12 | DI32
| 309 | 1401 | 2701-GZY-10004E | SDI0010-01R | 2701-GZY-10004E | - | 2701-GZY-10004E | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004E | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 13 | DI32
| 310 | 1401 | 2701-GZY-10004F | SDI0010-01R | 2701-GZY-10004F | - | 2701-GZY-10004F | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004F | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 14 | DI32
| 311 | 1401 | 2701-GZY-10004G | SDI0010-01R | 2701-GZY-10004G | - | 2701-GZY-10004G | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004G | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 15 | DI32
| 312 | 1401 | 2701-GZY-10004H | SDI0010-01R | 2701-GZY-10004H | - | 2701-GZY-10004H | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004H | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 16 | DI32
| 313 | 1401 | 2701-GZY-10004I | SDI0010-01R | 2701-GZY-10004I | - | 2701-GZY-10004I | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004I | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 17 | DI32
| 314 | 1401 | 2701-GZY-10004J | SDI0010-01R | 2701-GZY-10004J | - | 2701-GZY-10004J | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004J | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 18 | DI32
| 315 | 1401 | 2701-GZY-10004K | SDI0010-01R | 2701-GZY-10004K | - | 2701-GZY-10004K | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004K | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 19 | DI32
| 316 | 1401 | 2701-GZY-10004L | SDI0010-01R | 2701-GZY-10004L | - | 2701-GZY-10004L | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004L | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 20 | DI32
| 317 | 1401 | 2701-GZY-10004M | SDI0010-01R | 2701-GZY-10004M | - | 2701-GZY-10004M | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004M | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 21 | DI32
| 318 | 1401 | 2701-GZY-10004N | SDI0010-01R | 2701-GZY-10004N | - | 2701-GZY-10004N | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-10004M | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 22 | DI32
Изм 2026.06.19 Change io type DIR-VFC -> S | 320 | 1401 | 2701-HZS-11301 | SDO0001-01 | 2701-HZS-11301 | 2701-Z-11301 | 2701-HZS-11301 | Protection of fuel gas system interlock | Soft Push button | 2000-S-SC-B01 | 2490156-1401-PR007-0111A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add soft button |  |  | Z-11301 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 339 | 1402 | 2711-LZIA-00107 | SAI1000-01R | 2711-L-00107 | 2711-Z-00101/00102 | 2711-LZT-00107 | Level Meter @ the top of 2711-TK-1301A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 15850 | mm | 0 | 15850 | mm | - | 1400 | 13950 | - | mm | 1 | Rev1 change Tag No. |  | Xinhui | Z-00101/00102 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 3 | 2711-S-JB-B215/SIS | 8x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x2.5 | 2711-S-JB-B215 | SIS | 534 | BK | 05 | Rev3 change Tag No. | 1402 | 1402-WDZAN-DJYJP3YP3 8x2x2.5-0001 |  | 2711-S-JB-B215 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 14 | AI16H
| 340 | 1402 | 2711-LZIA-00107 | SAI1000-01R | 2711-L-00107 | - | 2711-LI-00107 | Level Meter @ the top of 2711-TK-1301A | Local Indicate | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | - | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 341 | 1402 | 2711-LZIA-00107 | SAI1000-01R | 2711-L-00107 | - | 2711-LIZA-00107 | Level Meter @ the top of 2711-TK-1301A | LEVEL INDICATION ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 342 | 1402 | 2711-LZIA-00107 | SAI1000-01R | 2711-L-00107 | - | 2711-LZAH-00107 | Level Meter @ the top of 2711-TK-1301A | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 343 | 1402 | 2711-LZIA-00107 | SAI1000-01R | 2711-L-00107 | - | 2711-LZAHH-00107 | Level Meter @ the top of 2711-TK-1301A | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 344 | 1402 | 2711-LZIA-00107 | SAI1000-01R | 2711-L-00107 | - | 2711-LZAL-00107 | Level Meter @ the top of 2711-TK-1301A | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 345 | 1402 | 2711-LZIA-00107 | SAI1000-01R | 2711-L-00107 | - | 2711-LZALL-00107 | Level Meter @ the top of 2711-TK-1301A | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 347 | 1402 | 2711-LZA-00101 | SDI0010-01R | 2711-L-00101 | 2711-Z-00101 | 2711-LZS-00101 | Level Switch (HH) @ 2711-TK-1301A | HIGH-HIGH LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00101 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 09 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 0 | DI32
| 348 | 1402 | 2711-LZA-00101 | SDI0010-01R | 2711-L-00101 | - | 2711-LZA-00101 | Level Switch (HH) @ 2711-TK-1301A | HIGH-HIGH LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 349 | 1402 | 2711-LZA-00101 | SDI0010-01R | 2711-L-00101 | - | 2711-LZAHH-00101 | Level Switch (HH) @ 2711-TK-1301A | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 351 | 1402 | 2711-LZA-00102 | SDI0010-01R | 2711-L-00102 | 2711-Z-00102 | 2711-LZS-00102 | Level Switch (LL) @ 2711-TK-1301A | LOW-LOW LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00102 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 10 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 7 | DI32
| 352 | 1402 | 2711-LZA-00102 | SDI0010-01R | 2711-L-00102 | - | 2711-LZA-00102 | Level Switch (LL) @ 2711-TK-1301A | LOW-LOW LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 353 | 1402 | 2711-LZA-00102 | SDI0010-01R | 2711-L-00102 | - | 2711-LZALL-00102 | Level Switch (LL) @ 2711-TK-1301A | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 355 | 1402 | 2711-XZY-00101 | SDO0001-01 | 2711-X-00101 | - | 2711-XZV-00101 | Switch Valve @ the inlet of 2711-TK-1301A | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 356 | 1402 | 2711-XZY-00101 | SDO0001-01 | 2711-X-00101 | 2711-Z-00101/00107/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00101 | Switch Valve @ the inlet of 2711-TK-1301A | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00101/00107/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 01 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 24 | DO32P
| 357 | 1402 | 2711-XZZSO-00101 | SDI0010-02R | 2711-X-00101 | - | 2711-XZZSO-00101 | Switch Valve @ the inlet of 2711-TK-1301A | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 07 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 12 | DI32
| 358 | 1402 | 2711-XZZSC-00101 | SDI0010-02R | 2711-X-00101 | - | 2711-XZZSC-00101 | Switch Valve @ the inlet of 2711-TK-1301A | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 01 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 13 | DI32
| 360 | 1402 | 2711-XZY-00102 | SDO0001-01 | 2711-X-00102 | - | 2711-XZV-00102 | Switch Valve @ the outlet of 2711-TK-1301A | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 361 | 1402 | 2711-XZY-00102 | SDO0001-01 | 2711-X-00102 | 2711-Z-00102/00107/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00102 | Switch Valve @ the outlet of 2711-TK-1301A | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00102/00107/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 02 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 0 | DO32P
| 362 | 1402 | 2711-XZZSO-00102 | SDI0010-02R | 2711-X-00102 | - | 2711-XZZSO-00102 | Switch Valve @ the outlet of 2711-TK-1301A | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 07 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 6 | DI32
| 363 | 1402 | 2711-XZZSC-00102 | SDI0010-02R | 2711-X-00102 | - | 2711-XZZSC-00102 | Switch Valve @ the outlet of 2711-TK-1301A | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 01 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 7 | DI32
| 365 | 1402 | 2711-HZS-00107A-1 | SDI0010-01R | 2711-HS-00107A | 2711-Z-00107 | 2711-HZS-00107A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001A | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00107 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 9 | DI32
| 367 | 1402 | 2711-HZS-00107B | SDI0010-01R | 2711-HS-00107B | 2711-Z-00107 | 2711-HZS-00107B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1402-ST007-0001A | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No.,change to Exd |  |  | Z-00107 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-B224/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2711-S-JB-B224 | SIS |  | BK | 01 | Rev1 New add | 1402 |  |  | 2711-S-JB-B224 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 7 | DI32
| 369 | 1402 | 2711-XZY-00104 | SDO0001-01 | 2711-X-00104 | - | 2711-XZV-00104 | Switch Valve @ the inlet of 2711-TK-1301B | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 370 | 1402 | 2711-XZY-00104 | SDO0001-01 | 2711-X-00104 | 2711-Z-00103/00108/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00104 | Switch Valve @ the inlet of 2711-TK-1301B | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00103/00108/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 03 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 1 | DO32P
| 371 | 1402 | 2711-XZZSO-00104 | SDI0010-02R | 2711-X-00104 | - | 2711-XZZSO-00104 | Switch Valve @ the inlet of 2711-TK-1301B | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 08 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 22 | DI32
| 372 | 1402 | 2711-XZZSC-00104 | SDI0010-02R | 2711-X-00104 | - | 2711-XZZSC-00104 | Switch Valve @ the inlet of 2711-TK-1301B | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 02 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 23 | DI32
| 374 | 1402 | 2711-XZY-00105 | SDO0001-01 | 2711-X-00105 | 2711-Z-00104/00108/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00105 | Switch Valve @ the outlet of 2711-TK-1301B | Solenoid valve | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00104/00108/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 04 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 2 | DO32P
| 375 | 1402 | 2711-XZY-00105 | SDO0001-01 | 2711-X-00105 | - | 2711-XZV-00105 | Switch Valve @ the outlet of 2711-TK-1301B | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | - | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 376 | 1402 | 2711-XZZSO-00105 | SDI0010-02R | 2711-X-00105 | - | 2711-XZZSO-00105 | Switch Valve @ the outlet of 2711-TK-1301B | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 08 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 8 | DI32
| 377 | 1402 | 2711-XZZSC-00105 | SDI0010-02R | 2711-X-00105 | - | 2711-XZZSC-00105 | Switch Valve @ the outlet of 2711-TK-1301B | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 02 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 9 | DI32
| 379 | 1402 | 2711-LZIA-00108 | SAI1000-01R | 2711-L-00108 | 2711-Z-00103/00104 | 2711-LZT-00108 | Level Meter @ the top of 2711-TK-1301B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 15850 | mm | 0 | 15850 | mm | - | 1400 | 13950 | - | mm | 1 | Rev1 change Tag No. |  | Xinhui | Z-00103/00104 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 3 | 2711-S-JB-B215/SIS | 8x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x2.5 | 2711-S-JB-B215 | SIS | 534 | BK | 01 | Rev3 change Tag No. | 1402 | 1402-WDZAN-DJYJP3YP3 8x2x2.5-0001 |  | 2711-S-JB-B215 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 15 | AI16H
| 380 | 1402 | 2711-LZIA-00108 | SAI1000-01R | 2711-L-00108 | - | 2711-LI-00108 | Level Meter @ the top of 2711-TK-1301B | Local Indicate | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | - | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 381 | 1402 | 2711-LZIA-00108 | SAI1000-01R | 2711-L-00108 | - | 2711-LIZA-00108 | Level Meter @ the top of 2711-TK-1301B | LEVEL INDICATION ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 382 | 1402 | 2711-LZIA-00108 | SAI1000-01R | 2711-L-00108 | - | 2711-LZAH-00108 | Level Meter @ the top of 2711-TK-1301B | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 383 | 1402 | 2711-LZIA-00108 | SAI1000-01R | 2711-L-00108 | - | 2711-LZAHH-00108 | Level Meter @ the top of 2711-TK-1301B | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 384 | 1402 | 2711-LZIA-00108 | SAI1000-01R | 2711-L-00108 | - | 2711-LZAL-00108 | Level Meter @ the top of 2711-TK-1301B | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 385 | 1402 | 2711-LZIA-00108 | SAI1000-01R | 2711-L-00108 | - | 2711-LZALL-00108 | Level Meter @ the top of 2711-TK-1301B | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 387 | 1402 | 2711-LZA-00103 | SDI0010-01R | 2711-L-00103 | 2711-Z-00103 | 2711-LZS-00103 | Level Switch (HH) @ 2711-TK-1301B | HIGH-HIGH LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00103 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 01 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 1 | DI32
| 388 | 1402 | 2711-LZA-00103 | SDI0010-01R | 2711-L-00103 | - | 2711-LZA-00103 | Level Switch (HH) @ 2711-TK-1301B | HIGH-HIGH LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 389 | 1402 | 2711-LZA-00103 | SDI0010-01R | 2711-L-00103 | - | 2711-LZAHH-00103 | Level Switch (HH) @ 2711-TK-1301B | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 391 | 1402 | 2711-LZA-00104 | SDI0010-01R | 2711-L-00104 | 2711-Z-00104 | 2711-LZS-00104 | Level Switch (LL) @ 2711-TK-1301B | LOW-LOW LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00104 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 02 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 8 | DI32
| 392 | 1402 | 2711-LZA-00104 | SDI0010-01R | 2711-L-00104 | - | 2711-LZA-00104 | Level Switch (LL) @ 2711-TK-1301B | LOW-LOW LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 393 | 1402 | 2711-LZA-00104 | SDI0010-01R | 2711-L-00104 | - | 2711-LZALL-00104 | Level Switch (LL) @ 2711-TK-1301B | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 395 | 1402 | 2711-HZS-00108A-1 | SDI0010-01R | 2711-HS-00108A | 2711-Z-00108 | 2711-HZS-00108A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001B | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00108 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 10 | DI32
| 397 | 1402 | 2711-HZS-00108B | SDI0010-01R | 2711-HS-00108B | 2711-Z-00108 | 2711-HZS-00108B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1402-ST007-0001B | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00108 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-B224/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2711-S-JB-B224 | SIS |  | BK | 02 | Rev1 New add | 1402 |  |  | 2711-S-JB-B224 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 3 | DI32
| 399 | 1402 | 2711-XZY-00107 | SDO0001-01 | 2711-X-00107 | - | 2711-XZV-00107 | Switch Valve @ the inlet of 2711-TK-1301C | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 400 | 1402 | 2711-XZY-00107 | SDO0001-01 | 2711-X-00107 | 2711-Z-00105/00109/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00107 | Switch Valve @ the inlet of 2711-TK-1301C | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00105/00109/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 05 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 25 | DO32P
| 401 | 1402 | 2711-XZZSO-00107 | SDI0010-02R | 2711-X-00107 | - | 2711-XZZSO-00107 | Switch Valve @ the inlet of 2711-TK-1301C | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 09 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 14 | DI32
| 402 | 1402 | 2711-XZZSC-00107 | SDI0010-02R | 2711-X-00107 | - | 2711-XZZSC-00107 | Switch Valve @ the inlet of 2711-TK-1301C | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 03 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 15 | DI32
| 404 | 1402 | 2711-XZY-00108 | SDO0001-01 | 2711-X-00108 | - | 2711-XZV-00108 | Switch Valve @ the outlet of 2711-TK-1301C | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 405 | 1402 | 2711-XZY-00108 | SDO0001-01 | 2711-X-00108 | 2711-Z-00106/00109/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00108 | Switch Valve @ the outlet of 2711-TK-1301C | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00106/00109/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 06 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 26 | DO32P
| 406 | 1402 | 2711-XZZSO-00108 | SDI0010-02R | 2711-X-00108 | - | 2711-XZZSO-00108 | Switch Valve @ the outlet of 2711-TK-1301C | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 09 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 0 | DI32
| 407 | 1402 | 2711-XZZSC-00108 | SDI0010-02R | 2711-X-00108 | - | 2711-XZZSC-00108 | Switch Valve @ the outlet of 2711-TK-1301C | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 03 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 1 | DI32
| 409 | 1402 | 2711-LZIA-00109 | SAI1000-01R | 2711-L-00109 | 2711-Z-00105/00106 | 2711-LZT-00109 | Level Meter @ the top of 2711-TK-1301C | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 15850 | mm | 0 | 15850 | mm | - | 1400 | 13950 | - | mm | 1 | Rev1 change Tag No. |  | Xinhui | Z-00105/00106 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 3 | 2711-S-JB-B215/SIS | 8x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x2.5 | 2711-S-JB-B215 | SIS | 534 | BK | 06 | Rev3 change Tag No. | 1402 | 1402-WDZAN-DJYJP3YP3 8x2x2.5-0001 |  | 2711-S-JB-B215 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 0 | AI16H
| 410 | 1402 | 2711-LZIA-00109 | SAI1000-01R | 2711-L-00109 | - | 2711-LI-00109 | Level Meter @ the top of 2711-TK-1301C | Local Indicate | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | - | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 411 | 1402 | 2711-LZIA-00109 | SAI1000-01R | 2711-L-00109 | - | 2711-LIZA-00109 | Level Meter @ the top of 2711-TK-1301C | LEVEL INDICATION ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 412 | 1402 | 2711-LZIA-00109 | SAI1000-01R | 2711-L-00109 | - | 2711-LZAH-00109 | Level Meter @ the top of 2711-TK-1301C | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 413 | 1402 | 2711-LZIA-00109 | SAI1000-01R | 2711-L-00109 | - | 2711-LZAHH-00109 | Level Meter @ the top of 2711-TK-1301C | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 414 | 1402 | 2711-LZIA-00109 | SAI1000-01R | 2711-L-00109 | - | 2711-LZAL-00109 | Level Meter @ the top of 2711-TK-1301C | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 415 | 1402 | 2711-LZIA-00109 | SAI1000-01R | 2711-L-00109 | - | 2711-LZALL-00109 | Level Meter @ the top of 2711-TK-1301C | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 new add |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 417 | 1402 | 2711-LZA-00105 | SDI0010-01R | 2711-L-00105 | 2711-Z-00105 | 2711-LZS-00105 | Level Switch (HH) @ 2711-TK-1301C | HIGH-HIGH LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00105 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 11 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 2 | DI32
| 418 | 1402 | 2711-LZA-00105 | SDI0010-01R | 2711-L-00105 | - | 2711-LZA-00105 | Level Switch (HH) @ 2711-TK-1301C | HIGH-HIGH LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 419 | 1402 | 2711-LZA-00105 | SDI0010-01R | 2711-L-00105 | - | 2711-LZAHH-00105 | Level Switch (HH) @ 2711-TK-1301C | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 421 | 1402 | 2711-LZA-00106 | SDI0010-01R | 2711-L-00106 | 2711-Z-00106 | 2711-LZS-00106 | Level Switch (LL) @ 2711-TK-1301C | LOW-LOW LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00106 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 12 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 9 | DI32
| 422 | 1402 | 2711-LZA-00106 | SDI0010-01R | 2711-L-00106 | - | 2711-LZA-00106 | Level Switch (LL) @ 2711-TK-1301C | LOW-LOW LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 423 | 1402 | 2711-LZA-00106 | SDI0010-01R | 2711-L-00106 | - | 2711-LZALL-00106 | Level Switch (LL) @ 2711-TK-1301C | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 425 | 1402 | 2711-HZS-00109A-1 | SDI0010-01R | 2711-HS-00109A | 2711-Z-00109 | 2711-HZS-00109A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001C | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00109 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 11 | DI32
| 427 | 1402 | 2711-HZS-00109B | SDI0010-01R | 2711-HS-00109B | 2711-Z-00109 | 2711-HZS-00109B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1402-ST007-0001C | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00109 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-B224/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2711-S-JB-B224 | SIS |  | BK | 03 | Rev1 New add | 1402 |  |  | 2711-S-JB-B224 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 4 | DI32
| 429 | 1402 | 2711-XZY-00401 | SDO0001-01 | 2711-X-00401 | - | 2711-XZV-00401 | Switch Valve @ the outlet of 2711-TK-1301C | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 430 | 1402 | 2711-XZY-00401 | SDO0001-01 | 2711-X-00401 | 2711-Z-00401/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00401 | Switch Valve @ the outlet of 2711-TK-1301C | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00401/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 07 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 27 | DO32P
| 431 | 1402 | 2711-XZZSO-00401 | SDI0010-02R | 2711-X-00401 | - | 2711-XZZSO-00401 | Switch Valve @ the outlet of 2711-TK-1301C | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 10 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 16 | DI32
| 432 | 1402 | 2711-XZZSC-00401 | SDI0010-02R | 2711-X-00401 | - | 2711-XZZSC-00401 | Switch Valve @ the outlet of 2711-TK-1301C | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 04 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 17 | DI32
| 434 | 1402 | 2711-XZY-00402 | SDO0001-01 | 2711-X-00402 | - | 2711-XZV-00402 | Switch Valve @ the outlet of 2711-TK-1302 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 435 | 1402 | 2711-XZY-00402 | SDO0001-01 | 2711-X-00402 | 2711-Z-00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-XZY-00402 | Switch Valve @ the outlet of 2711-TK-1302 | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 08 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 30 | DO32P
| 436 | 1402 | 2711-XZZSO-00402 | SDI0010-02R | 2711-X-00402 | - | 2711-XZZSO-00402 | Switch Valve @ the outlet of 2711-TK-1302 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 10 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 4 | DI32
| 437 | 1402 | 2711-XZZSC-00402 | SDI0010-02R | 2711-X-00402 | - | 2711-XZZSC-00402 | Switch Valve @ the outlet of 2711-TK-1302 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 04 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 5 | DI32
| 439 | 1402 | 2711-LZIA-00403 | SAI1000-01R | 2711-L-00403 | 2711-Z-00401/00402 | 2711-LZT-00403 | Level Meter @ the top of 2711-TK-1302 | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 15850 | mm | 0 | 15850 | mm | - | 1400 | 13950 | - | mm | 1 | Rev1 change Tag No. |  | Xinhui | Z-00401/00402 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 3 | 2711-S-JB-B215/SIS | 8x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x2.5 | 2711-S-JB-B215 | SIS | 534 | BK | 02 | Rev3 change Tag No. | 1402 | 1402-WDZAN-DJYJP3YP3 8x2x2.5-0001 |  | 2711-S-JB-B215 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 1 | AI16H
| 440 | 1402 | 2711-LZIA-00403 | SAI1000-01R | 2711-L-00403 | - | 2711-LZA-00403 | Level Meter @ the top of 2711-TK-1302 | LEVEL INDICATION ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 441 | 1402 | 2711-LZIA-00403 | SAI1000-01R | 2711-L-00403 | - | 2711-LZAHH-00403 | Level Meter @ the top of 2711-TK-1302 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 442 | 1402 | 2711-LZIA-00403 | SAI1000-01R | 2711-L-00403 | - | 2711-LZAH-00403 | Level Meter @ the top of 2711-TK-1302 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 443 | 1402 | 2711-LZIA-00403 | SAI1000-01R | 2711-L-00403 | - | 2711-LZAL-00403 | Level Meter @ the top of 2711-TK-1302 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 444 | 1402 | 2711-LZIA-00403 | SAI1000-01R | 2711-L-00403 | - | 2711-LZALL-00403 | Level Meter @ the top of 2711-TK-1302 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 446 | 1402 | 2711-LZA-00401 | SDI0010-01R | 2711-L-00401 | 2711-Z-00401 | 2711-LZS-00401 | Level Switch (HH) @ 2711-TK-1302 | HIGH-HIGH LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00401 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 03 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 3 | DI32
| 447 | 1402 | 2711-LZA-00401 | SDI0010-01R | 2711-L-00401 | - | 2711-LZA-00401 | Level Switch (HH) @ 2711-TK-1302 | HIGH-HIGH LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 448 | 1402 | 2711-LZA-00401 | SDI0010-01R | 2711-L-00401 | - | 2711-LZAHH-00401 | Level Switch (HH) @ 2711-TK-1302 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 450 | 1402 | 2711-LZA-00402 | SDI0010-01R | 2711-L-00402 | 2711-Z-00402 | 2711-LZS-00402 | Level Switch (LL) @ 2711-TK-1302 | LOW-LOW LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00402 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 04 | Rev1 change cable length | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 10 | DI32
| 451 | 1402 | 2711-LZA-00402 | SDI0010-01R | 2711-L-00402 | - | 2711-LZA-00402 | Level Switch (LL) @ 2711-TK-1302 | LOW-LOW LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 452 | 1402 | 2711-LZA-00402 | SDI0010-01R | 2711-L-00402 | - | 2711-LZALL-00402 | Level Switch (LL) @ 2711-TK-1302 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 454 | 1402 | 2711-HZS-00401A-1 | SDI0010-01R | 2711-HS-00401A | 2711-Z-00403 | 2711-HZS-00401A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0004 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00403 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 12 | DI32
| 456 | 1402 | 2711-HZS-00401B | SDI0010-01R | 2711-HS-00401B | 2711-Z-00403 | 2711-HZS-00401B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1402-ST007-0004 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00403 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-B224/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2711-S-JB-B224 | SIS |  | BK | 04 | Rev1 New add | 1402 |  |  | 2711-S-JB-B224 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 5 | DI32
| 458 | 1402 | 2711-XZY-00501 | SDO0001-01 | 2711-X-00501 | - | 2711-XZV-00501 | Switch Valve @ the inlet of 2711-TK-1303 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 459 | 1402 | 2711-XZY-00501 | SDO0001-01 | 2711-X-00501 | 2711-Z-00501/00503/00211/00212/00311/00312/00313 | 2711-XZY-00501 | Switch Valve @ the inlet of 2711-TK-1303 | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00501/00503/00211/00212/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 09 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 28 | DO32P
| 460 | 1402 | 2711-XZZSO-00501 | SDI0010-02R | 2711-X-00501 | - | 2711-XZZSO-00501 | Switch Valve @ the inlet of 2711-TK-1303 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 11 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 18 | DI32
| 461 | 1402 | 2711-XZZSC-00501 | SDI0010-02R | 2711-X-00501 | - | 2711-XZZSC-00501 | Switch Valve @ the inlet of 2711-TK-1303 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 05 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 21 | DI32
| 463 | 1402 | 2711-XZY-00502 | SDO0001-01 | 2711-X-00502 | - | 2711-XZV-00502 | Switch Valve @ the outlet of 2711-TK-1303 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 464 | 1402 | 2711-XZY-00502 | SDO0001-01 | 2711-X-00502 | 2711-Z-00502/00503/00211/00212/00311/00312/00313 | 2711-XZY-00502 | Switch Valve @ the outlet of 2711-TK-1303 | Solenoid Valve | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00502/00503/00211/00212/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 10 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 31 | DO32P
| 465 | 1402 | 2711-XZZSO-00502 | SDI0010-02R | 2711-X-00502 | - | 2711-XZZSO-00502 | Switch Valve @ the outlet of 2711-TK-1303 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 11 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 2 | DI32
| 466 | 1402 | 2711-XZZSC-00502 | SDI0010-02R | 2711-X-00502 | - | 2711-XZZSC-00502 | Switch Valve @ the outlet of 2711-TK-1303 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 05 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 3 | DI32
| 468 | 1402 | 2711-LZIA-00503 | SAI1000-01R | 2711-L-00503 | 2711-Z-00501/00502 | 2711-LZT-00503 | Level Meter @ the top of 2711-TK-1303 | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 11500 | mm | 0 | 11500 | mm | - | 900 | 9970 | - | mm | 1 | Rev1 change Tag No. |  | Xinhui | Z-00501/00502 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 3 | 2711-S-JB-B215/SIS | 8x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x2.5 | 2711-S-JB-B215 | SIS | 534 | BK | 03 | Rev3 change Tag No. | 1402 | 1402-WDZAN-DJYJP3YP3 8x2x2.5-0001 |  | 2711-S-JB-B215 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 2 | AI16H
| 469 | 1402 | 2711-LZIA-00503 | SAI1000-01R | 2711-L-00503 | - | 2711-LZA-00503 | Level Meter @ the top of 2711-TK-1303 | LEVEL INDICATION ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 470 | 1402 | 2711-LZIA-00503 | SAI1000-01R | 2711-L-00503 | - | 2711-LZAHH-00503 | Level Meter @ the top of 2711-TK-1303 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 471 | 1402 | 2711-LZIA-00503 | SAI1000-01R | 2711-L-00503 | - | 2711-LZAH-00503 | Level Meter @ the top of 2711-TK-1303 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 472 | 1402 | 2711-LZIA-00503 | SAI1000-01R | 2711-L-00503 | - | 2711-LZAL-00503 | Level Meter @ the top of 2711-TK-1303 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 473 | 1402 | 2711-LZIA-00503 | SAI1000-01R | 2711-L-00503 | - | 2711-LZALL-00503 | Level Meter @ the top of 2711-TK-1303 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 475 | 1402 | 2711-LZA-00501 | SDI0010-01R | 2711-L-00501 | 2711-Z-00501 | 2711-LZS-00501 | Level Switch (HH) @ 2711-TK-1303 | HIGH-HIGH LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00501 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 05 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 4 | DI32
| 476 | 1402 | 2711-LZA-00501 | SDI0010-01R | 2711-L-00501 | - | 2711-LZA-00501 | Level Switch (HH) @ 2711-TK-1303 | HIGH-HIGH LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 477 | 1402 | 2711-LZA-00501 | SDI0010-01R | 2711-L-00501 | - | 2711-LZAHH-00501 | Level Switch (HH) @ 2711-TK-1303 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 479 | 1402 | 2711-LZA-00502 | SDI0010-01R | 2711-L-00502 | 2711-Z-00502 | 2711-LZS-00502 | Level Switch (LL) @ 2711-TK-1303 | LOW-LOW LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00502 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 06 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 11 | DI32
| 480 | 1402 | 2711-LZA-00502 | SDI0010-01R | 2711-L-00502 | - | 2711-LZA-00502 | Level Switch (LL) @ 2711-TK-1303 | LOW-LOW LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 481 | 1402 | 2711-LZA-00502 | SDI0010-01R | 2711-L-00502 | - | 2711-LZALL-00502 | Level Switch (LL) @ 2711-TK-1303 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 483 | 1402 | 2711-HZS-00501A-1 | SDI0010-01R | 2711-HS-00501A | 2711-Z-00503 | 2711-HZS-00501A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0005 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00503 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 13 | DI32
| 485 | 1402 | 2711-HZS-00501B | SDI0010-01R | 2711-HS-00501B | 2711-Z-00503 | 2711-HZS-00501B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1402-ST007-0005 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00503 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-B224/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2711-S-JB-B224 | SIS |  | BK | 05 | Rev1 New add | 1402 |  |  | 2711-S-JB-B224 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 6 | DI32
| 487 | 1402 | 2711-XZY-00601 | SDO0001-01 | 2711-X-00601 | - | 2711-XZV-00601 | Switch Valve @ the inlet of 2711-TK-1306 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 488 | 1402 | 2711-XZY-00601 | SDO0001-01 | 2711-X-00601 | 2711-Z-00601/00603/00211/00212/00311/00312/00313 | 2711-XZY-00601 | Switch Valve @ the inlet of 2711-TK-1306 | Solenoid valve | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00601/00603/00211/00212/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 11 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 29 | DO32P
| 489 | 1402 | 2711-XZZSO-00601 | SDI0010-02R | 2711-X-00601 | - | 2711-XZZSO-00601 | Switch Valve @ the inlet of 2711-TK-1306 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 12 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 19 | DI32
| 490 | 1402 | 2711-XZZSC-00601 | SDI0010-02R | 2711-X-00601 | - | 2711-XZZSC-00601 | Switch Valve @ the inlet of 2711-TK-1306 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C218/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C218 | SIS | 539 | BU | 06 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2711-S-JB-C218 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 20 | DI32
| 492 | 1402 | 2711-XZY-00602 | SDO0001-01 | 2711-X-00602 | - | 2711-XZV-00602 | Switch Valve @ the outlet of 2711-TK-1306 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 493 | 1402 | 2711-XZY-00602 | SDO0001-01 | 2711-X-00602 | 2711-Z-00602/00603/00211/00212/00311/00312/00313 | 2711-XZY-00602 | Switch Valve @ the outlet of 2711-TK-1306 | Solenoid valve | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00602/00603/00211/00212/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-D211/SIS | 37x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2711-S-JB-D211 | SIS | 534 | BK | 12 |  | 1402 | 1402-WDZAN-KYJYP3 37x2.5-0001 |  | 2711-S-JB-D211 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 3 | DO32P
| 494 | 1402 | 2711-XZZSO-00602 | SDI0010-02R | 2711-X-00602 | - | 2711-XZZSO-00602 | Switch Valve @ the outlet of 2711-TK-1306 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 12 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 10 | DI32
| 495 | 1402 | 2711-XZZSC-00602 | SDI0010-02R | 2711-X-00602 | - | 2711-XZZSC-00602 | Switch Valve @ the outlet of 2711-TK-1306 | Limit Switch | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change to DIR-NAMUR |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C217/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C217 | SIS | 560 | BU | 06 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2711-S-JB-C217 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 11 | DI32
| 497 | 1402 | 2711-LZIA-00603 | SAI1000-01R | 2711-L-00603 | 2711-Z-00601/00602 | 2711-LZT-00603 | Level Meter @ the top of 2711-TK-1306 | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 6000 | mm | 0 | 6000 | mm | - | 1440 | 4930 | - | mm | 1 | Rev1 change Tag No. |  | Xinhui | Z-00601/00602 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 3 | 2711-S-JB-B215/SIS | 8x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x2.5 | 2711-S-JB-B215 | SIS | 534 | BK | 04 | Rev3 change Tag No. | 1402 | 1402-WDZAN-DJYJP3YP3 8x2x2.5-0001 |  | 2711-S-JB-B215 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 3 | AI16H
| 498 | 1402 | 2711-LZIA-00603 | SAI1000-01R | 2711-L-00603 | - | 2711-LZA-00603 | Level Meter @ the top of 2711-TK-1306 | LEVEL INDICATION ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 499 | 1402 | 2711-LZIA-00603 | SAI1000-01R | 2711-L-00603 | - | 2711-LZAHH-00603 | Level Meter @ the top of 2711-TK-1306 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 500 | 1402 | 2711-LZIA-00603 | SAI1000-01R | 2711-L-00603 | - | 2711-LZAH-00603 | Level Meter @ the top of 2711-TK-1306 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 501 | 1402 | 2711-LZIA-00603 | SAI1000-01R | 2711-L-00603 | - | 2711-LZAL-00603 | Level Meter @ the top of 2711-TK-1306 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 502 | 1402 | 2711-LZIA-00603 | SAI1000-01R | 2711-L-00603 | - | 2711-LZALL-00603 | Level Meter @ the top of 2711-TK-1306 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 change Tag No. |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 504 | 1402 | 2711-LZA-00601 | SDI0010-01R | 2711-L-00601 | 2711-Z-00601 | 2711-LZS-00601 | Level Switch (HH) @ 2711-TK-1306 | HIGH-HIGH LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00601 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 07 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 5 | DI32
| 505 | 1402 | 2711-LZA-00601 | SDI0010-01R | 2711-L-00601 | - | 2711-LZA-00601 | Level Switch (HH) @ 2711-TK-1306 | HIGH-HIGH LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 506 | 1402 | 2711-LZA-00601 | SDI0010-01R | 2711-L-00601 | - | 2711-LZAHH-00601 | Level Switch (HH) @ 2711-TK-1306 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 508 | 1402 | 2711-LZA-00602 | SDI0010-01R | 2711-L-00602 | 2711-Z-00602 | 2711-LZS-00602 | Level Switch (LL) @ 2711-TK-1306 | LOW-LOW LEVEL SWITCH | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00602 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C219/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2711-S-JB-C219 | SIS | 564 | BU | 08 |  | 1402 | 1402-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2711-S-JB-C219 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 6 | DI32
| 509 | 1402 | 2711-LZA-00602 | SDI0010-01R | 2711-L-00602 | - | 2711-LZA-00602 | Level Switch (LL) @ 2711-TK-1306 | LOW-LOW LEVEL SWITCH ALARM | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 510 | 1402 | 2711-LZA-00602 | SDI0010-01R | 2711-L-00602 | - | 2711-LZALL-00602 | Level Switch (LL) @ 2711-TK-1306 | Alarm:SIS | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版
| 512 | 1402 | 2711-HZS-00601A-1 | SDI0010-01R | 2711-HS-00601A | 2711-Z-00603 | 2711-HZS-00601A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0006 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev3 change Tag No. Rev1 change Tag No. |  |  | Z-00603 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 14 | DI32
| 514 | 1402 | 2711-HZS-00603B | SDI0010-01R | 2711-HS-00601B | 2711-Z-00603 | 2711-HZS-00603B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1402-ST007-0006 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00603 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | 1 | 2711-S-JB-B224/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2711-S-JB-B224 | SIS |  | BK | 06 | Rev1 New add | 1402 |  |  | 2711-S-JB-B224 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 8 | DI32
| 516 | 1402 | 2711-PZIA-00961 | SAI1000-01R | 2711-P-00961 | - | 2711-PZT-00961 | Seal auxiliary system of 2711-P-1311 | PRESSURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 0,3 | Mpag | - | - | - | - | - | 0,1 | - | Mpag | 1 | Rev1 Tag change,AIR | 2711-P-1311 | VINCI |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C301/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2711-S-JB-C301 | SIS |  | BU |  | Rev1 new add for package | 1402 |  |  | 2711-S-JB-C301 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 10 | AI16H
| 517 | 1402 | 2711-LZIA-00961 | SAI1000-01R | 2711-L-00961 | - | 2711-LZT-00961 | Seal auxiliary system of 2711-P-1311 | D/P LEVEL TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | - | - | - | 0 | 400 | mmH2O | - | 64 | 281 | - | mmH2O | 1 | Rev1 Tag change,AIR | 2711-P-1311 | VINCI |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C301/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2711-S-JB-C301 | SIS |  | BU |  | Rev1 new add for package | 1402 |  |  | 2711-S-JB-C301 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 11 | AI16H
| 518 | 1402 | 2711-TZIA-00961 | SAI1000-01R | 2711-T-00961 | - | 2711-TZT-00961 | Bearing temperature of 2711-P-1311 | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 150 | ℃ | - | - | - | - | - | 85 | - | ℃ | 2 | Rev2 Change service Rev1 Tag change | 2711-P-1311 | VINCI |  | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 |  | 2711-S-JB-C301/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2711-S-JB-C301 | SIS |  | BU |  | Rev1 new add for package | 1402 |  |  | 2711-S-JB-C301 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 12 | AI16H
| 520 | 1402 | 2711-MXI-01301A | SDO0001-01 | 2711-MXI-01301A | 2711-Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-01301A | SM Loading Pump 2711-P-1301A Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0002 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 0 | DO32P
| 521 | 1402 | 2711-MXI-11301A | SDO0001-01 | 2711-MXI-11301A | 2711-Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-11301A | SM Loading Pump 2711-P-1301B Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0002 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 1 | DO32P
| 522 | 1402 | 2711-MXI-01302A | SDO0001-01 | 2711-MXI-01302A | 2711-Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-01302A | SM Transfer Pump 2711-P-1302A Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0002 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 2 | DO32P
| 523 | 1402 | 2711-MXI-11302A | SDO0001-01 | 2711-MXI-11302A | 2711-Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-11302A | SM Transfer Pump 2711-P-1302B Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0002 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 3 | DO32P
| 524 | 1402 | 2711-MXI-01303A | SDO0001-01 | 2711-MXI-01303A | 2711-Z-00102/00107/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-01303A | SM Circulating Pump 2711-P-1303A Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0001A | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102/00107/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 4 | DO32P
| 525 | 1402 | 2711-MXI-11303A | SDO0001-01 | 2711-MXI-11303A | 2711-Z-00104/00108/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-11303A | SM Circulating Pump 2711-P-1303B Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0001B | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00104/00108/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 5 | DO32P
| 526 | 1402 | 2711-MXI-21303A | SDO0001-01 | 2711-MXI-21303A | 2711-Z-00106/00109/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-21303A | SM Circulating Pump 2711-P-1303C Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0001C | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00106/00109/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 6 | DO32P
| 527 | 1402 | 2711-MXI-41303A | SDO0001-01 | 2711-MXI-41303A | 2711-Z-00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-41303A | SM Circulating Pump 2711-P-1303E Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0004 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 7 | DO32P
| 528 | 1402 | 2711-MXI-01304A | SDO0001-01 | 2711-MXI-01304A | 2711-Z-00502/00503/00211/00212/00311/00312/00313 | 2711-MXI-01304A | EB Transfer Pump 2711-P-1304A Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0005 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00502/00503/00211/00212/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 8 | DO32P
| 529 | 1402 | 2711-MXI-11304A | SDO0001-01 | 2711-MXI-11304A | 2711-Z-00502/00503/00211/00212/00311/00312/00313 | 2711-MXI-11304A | EB Transfer Pump 2711-P-1304B Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0005 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00502/00503/00211/00212/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 9 | DO32P
| 530 | 1402 | 2711-MXI-01307A | SDO0001-01 | 2711-MXI-01307A | 2711-Z-00602/00603/00211/00212/00311/00312/00313 | 2711-MXI-01307A | Oligomer Loading Pump 2711-P-1307 Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0006 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00602/00603/00211/00212/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 10 | DO32P
| 531 | 1402 | 2711-MXI-01308A | SDO0001-01 | 2711-MXI-01308A | 2711-Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | 2711-MXI-01308A | SM Loading Pump 2711-P-1308 Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0001C | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102/00104/00106/00107/00108/00109/00402/00403/00111/00112/00113/00114/00115/00116/00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 11 | DO32P
| 532 | 1402 | 2711-MXI-01311A | SDO0001-01 | 2711-MXI-01311A | 2711-Z-00311/00312/00313 | 2711-MXI-01311A | Drain Pump 2711-P-1311 Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | 2490156-1402-PR007-0007 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00311/00312/00313 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 12 | DO32P
| 534 | 1402 | 2711-GZY-00111 | SDI0010-01R | 2711-GZY-00111 | 2711-Z-00111 | 2711-GZY-00111 | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00111 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 23 | DI32
| 535 | 1402 | 2711-GZY-00211 | SDI0010-01R | 2711-GZY-00211 | 2711-Z-00211 | 2711-GZY-00211 | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00211 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 24 | DI32
| 536 | 1402 | 2711-GZY-00311 | SDI0010-01R | 2711-GZY-00311 | 2711-Z-00311 | 2711-GZY-00311 | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00311 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 25 | DI32
| 551 | 1702 | 2712-XZY-00104 | SDO0001-01 | 2712-X-00104 | - | 2712-XZV-00104 | Switch valve @ the recirculation line of styrene | ON-OFF VALVE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版
| 552 | 1702 | 2712-XZY-00104 | SDO0001-01 | 2712-X-00104 | Z-00102/00111/00112 | 2712-XZY-00104 | Switch valve @ the recirculation line of styrene | Solenoid valve | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00102/00111/00112 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-D426/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2712-S-JB-D426 | SIS | 544 | BK | 04 |  | 1702 | 1011 |  | 2712-S-JB-D426 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 23 | DO32P
| 553 | 1702 | 2712-XZZSC-00104 | SDI0010-02R | 2712-X-00104 | - | 2712-XZZSC-00104 | Switch valve @ the recirculation line of styrene | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 04 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 24 | DI32
| 554 | 1702 | 2712-XZZSO-00104 | SDI0010-02R | 2712-X-00104 | - | 2712-XZZSO-00104 | Switch valve @ the recirculation line of styrene | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 08 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 25 | DI32
| 556 | 1702 | 2712-XZY-00103 | SDO0001-01 | 2712-X-00103 | - | 2712-XZV-00103 | Switch valve @ the styrene line from 1402 | ON-OFF VALVE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版
| 557 | 1702 | 2712-XZY-00103 | SDO0001-01 | 2712-X-00103 | Z-00102/00111/00112 | 2712-XZY-00103 | Switch valve @ the styrene line from 1402 | Solenoid valve | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00102/00111/00112 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-D426/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2712-S-JB-D426 | SIS | 544 | BK | 03 |  | 1702 | 1011 |  | 2712-S-JB-D426 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 24 | DO32P
| 558 | 1702 | 2712-XZZSC-00103 | SDI0010-02R | 2712-X-00103 | - | 2712-XZZSC-00103 | Switch valve @ the styrene line from 1402 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 03 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 26 | DI32
| 559 | 1702 | 2712-XZZSO-00103 | SDI0010-02R | 2712-X-00103 | - | 2712-XZZSO-00103 | Switch valve @ the styrene line from 1402 | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 07 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 27 | DI32
| 561 | 1702 | 2712-XZY-00101 | SDO0001-01 | 2712-X-00101 | - | 2712-XZV-00101 | Switch valve @ the oligomer line from 1402 | ON-OFF VALVE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版
| 562 | 1702 | 2712-XZY-00101 | SDO0001-01 | 2712-X-00101 | Z-00101/00111/00112 | 2712-XZY-00101 | Switch valve @ the oligomer line from 1402 | Solenoid valve | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00101/00111/00112 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-D426/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2712-S-JB-D426 | SIS | 544 | BK | 01 |  | 1702 | 1011 |  | 2712-S-JB-D426 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 25 | DO32P
| 563 | 1702 | 2712-XZZSC-00101 | SDI0010-02R | 2712-X-00101 | - | 2712-XZZSC-00101 | Switch valve @ the oligomer line from 1402 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 01 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 28 | DI32
| 564 | 1702 | 2712-XZZSO-00101 | SDI0010-02R | 2712-X-00101 | - | 2712-XZZSO-00101 | Switch valve @ the oligomer line from 1402 | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 05 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 29 | DI32
| 566 | 1702 | 2712-XZY-00102 | SDO0001-01 | 2712-X-00102 | - | 2712-XZV-00102 | Switch valve @ the oligomer line from PS plant | ON-OFF VALVE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版
| 567 | 1702 | 2712-XZY-00102 | SDO0001-01 | 2712-X-00102 | Z-00101/00111/00112 | 2712-XZY-00102 | Switch valve @ the oligomer line from PS plant | Solenoid valve | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00101/00111/00112 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-D426/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2712-S-JB-D426 | SIS | 544 | BK | 02 |  | 1702 | 1011 |  | 2712-S-JB-D426 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 26 | DO32P
| 568 | 1702 | 2712-XZZSC-00102 | SDI0010-02R | 2712-X-00102 | - | 2712-XZZSC-00102 | Switch valve @ the oligomer line from PS plant | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 02 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 0 | DI32
| 569 | 1702 | 2712-XZZSO-00102 | SDI0010-02R | 2712-X-00102 | - | 2712-XZZSO-00102 | Switch valve @ the oligomer line from PS plant | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1702-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 |  | 2712-S-JB-C423/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2712-S-JB-C423 | SIS | 544 | BU | 06 |  | 1702 | 994 |  | 2712-S-JB-C423 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 1 | DI32
| 571 | 1702 | 2712-HZS-00101B | SDI0010-01R | 2712-HZS-00101B | Z-00101 | 2712-HZS-00101B | Emergency Shutdown Pushbutton | PUSH BUTTON | 2000-S-SC-B01 | 2490156-1702-ST007-0001 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update Tag No. |  |  | Z-00101 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | 1 | 2712-S-JB-B429/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2712-S-JB-B429 | SIS |  | BK | 01 | Rev1 new add | 1702 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 0 | DI32
| 572 | 1702 | 2712-HZS-00101A-1 | SDI0010-01R | 2712-HZS-00101A | Z-00101 | 2712-HZS-00101A-1 | Emergency Shutdown Pushbutton | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1702-ST007-0001 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00101 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 15 | DI32
| 574 | 1702 | 2712-HZS-00102B | SDI0010-01R | 2712-HZS-00102B | Z-00102 | 2712-HZS-00102B | Emergency Shutdown Pushbutton | PUSH BUTTON | 2000-S-SC-B01 | 2490156-1702-ST007-0001 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | 1 | 2712-S-JB-B429/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2712-S-JB-B429 | SIS |  | BK | 02 | Rev1 new add | 1702 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 1 | DI32
| 575 | 1702 | 2712-HZS-00102A-1 | SDI0010-01R | 2712-HZS-00102A | Z-00102 | 2712-HZS-00102A-1 | Emergency Shutdown Pushbutton | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1702-ST007-0001 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 16 | DI32
| 577 | 1702 | 2712-PZIA-00961 | SAI1000-01R | 2712-P-00961 | - | 2712-PZT-00961 | Seal auxiliary system of 2712-P-0001 | PRESSURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 0,3 | Mpag | - | - | - | - | - | 0,1 | - | Mpag | 1 | Rev1 Tag change | 2712-P-0001 | VINCI |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | 1 | 2712-S-JB-C401/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2712-S-JB-C401 | SIS |  | BU |  | Rev1 new add for package | [5 empty] | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 2 | AI16H
| 578 | 1702 | 2712-LZIA-00961 | SAI1000-01R | 2712-L-00961 | - | 2712-LZT-00961 | Seal auxiliary system of 2712-P-0001 | LEVEL TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | - | - | - | 0 | 400 | mmH2O | - | 64 | 281 | - | mmH2O | 1 | Rev1 Tag change | 2712-P-0001 | VINCI |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | 1 | 2712-S-JB-C401/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2712-S-JB-C401 | SIS |  | BU |  | Rev1 new add for package | [5 empty] | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 3 | AI16H
| 579 | 1702 | 2712-TZIA-00961 | SAI1000-01R | 2712-T-00961 | - | 2712-TZT-00961 | Bearing temperature of 2712-P-0001 | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 150 | ℃ | - | - | - | - | - | 85 | - | ℃ | 2 | Rev2 Change service Rev1 Tag change | 2712-P-0001 | VINCI |  | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | 1 | 2712-S-JB-C401/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2712-S-JB-C401 | SIS |  | BU |  | Rev1 new add for package | [5 empty] | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 4 | AI16H
| 581 | 1702 | 2712-GZY-00111 | SDI0010-01R | 2712-GZY-00111 | Z-00111/00112 | 2712-GZY-00111 | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00111/00112 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 26 | DI32
| 584 | 1702 | 2712-MXI-0001A | SDO0001-01 | 2712-MXI-0001A | Z-00111/00112 | 2712-MXI-00001A | Drain Pump 2712-P-0001 Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | 2490156-1702-ST007-0003 | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 Change Tag No. Rev2 New add |  |  | Z-00111/00112 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [14 empty] | ? | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 11 | DO32P
| 586 | 1703 | 2713-XZY-01001 | SDO0001-01 | 2713-X-01001 | - | 2713-XZV-01001 | Switch valve @ the out let ar from 2713-P-0001A/B | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版
| 587 | 1703 | 2713-XZY-01001 | SDO0001-01 | 2713-X-01001 | Z-01001 | 2713-XZY-01001 | Switch valve @ the out let ar from 2713-P-0001A/B | Solenoid valve | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-01001 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-D463/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2713-S-JB-D463 | SIS | 583 | BK | 05 |  | 1703 | 1340 |  | 2713-S-JB-D463 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 27 | DO32P
| 588 | 1703 | 2713-XZZSO-01001 | SDI0010-02R | 2713-X-01001 | - | 2713-XZZSO-01001 | Switch valve @ the out let ar from 2713-P-0001A/B | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 10 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 2 | DI32
| 589 | 1703 | 2713-XZZSC-01001 | SDI0010-02R | 2713-X-01001 | - | 2713-XZZSC-01001 | Switch valve @ the out let ar from 2713-P-0001A/B | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 05 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 3 | DI32
| 591 | 1703 | 2713-XZY-00101 | SDO0001-01 | 2713-X-00101 | - | 2713-XZV-00101 | Switch valve @ the inlet of styrene from 1402 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版
| 592 | 1703 | 2713-XZY-00101 | SDO0001-01 | 2713-X-00101 | Z-00101 | 2713-XZY-00101 | Switch valve @ the inlet of styrene from 1402 | Solenoid valve | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00101 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-D463/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2713-S-JB-D463 | SIS | 583 | BK | 01 |  | 1703 | 1340 |  | 2713-S-JB-D463 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 28 | DO32P
| 593 | 1703 | 2713-XZZSO-00101 | SDI0010-02R | 2713-X-00101 | - | 2713-XZZSO-00101 | Switch valve @ the inlet of styrene from 1402 | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 06 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 4 | DI32
| 594 | 1703 | 2713-XZZSC-00101 | SDI0010-02R | 2713-X-00101 | - | 2713-XZZSC-00101 | Switch valve @ the inlet of styrene from 1402 | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 01 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 5 | DI32
| 596 | 1703 | 2713-XZY-00701 | SDO0001-01 | 2713-X-00701 | - | 2713-XZV-00701 | Switch valve @ the inlet of TB from 1401 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版
| 597 | 1703 | 2713-XZY-00701 | SDO0001-01 | 2713-X-00701 | Z-00701 | 2713-XZY-00701 | Switch valve @ the inlet of TB from 1401 | Solenoid valve | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00701 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-D463/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2713-S-JB-D463 | SIS | 583 | BK | 03 |  | 1703 | 1340 |  | 2713-S-JB-D463 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 29 | DO32P
| 598 | 1703 | 2713-XZZSO-00701 | SDI0010-02R | 2713-X-00701 | - | 2713-XZZSO-00701 | Switch valve @ the inlet of TB from 1401 | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 08 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 6 | DI32
| 599 | 1703 | 2713-XZZSC-00701 | SDI0010-02R | 2713-X-00701 | - | 2713-XZZSC-00701 | Switch valve @ the inlet of TB from 1401 | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 03 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 7 | DI32
| 601 | 1703 | 2713-XZY-00702 | SDO0001-01 | 2713-X-00702 | - | 2713-XZV-00702 | Switch valve @ the inlet of tar from 1401 | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版
| 602 | 1703 | 2713-XZY-00702 | SDO0001-01 | 2713-X-00702 | Z-00702 | 2713-XZY-00702 | Switch valve @ the inlet of tar from 1401 | Solenoid valve | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00702 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-D463/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2713-S-JB-D463 | SIS | 583 | BK | 04 |  | 1703 | 1340 |  | 2713-S-JB-D463 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 30 | DO32P
| 603 | 1703 | 2713-XZZSO-00702 | SDI0010-02R | 2713-X-00702 | - | 2713-XZZSO-00702 | Switch valve @ the inlet of tar from 1401 | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 09 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 8 | DI32
| 604 | 1703 | 2713-XZZSC-00702 | SDI0010-02R | 2713-X-00702 | - | 2713-XZZSC-00702 | Switch valve @ the inlet of tar from 1401 | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 04 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 9 | DI32
| 606 | 1703 | 2713-XZY-00105 | SDO0001-01 | 2713-X-00105 | - | 2713-XZV-00105 | Switch valve @ the recirculation line of styrene | On-Off valve:Ball | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版
| 607 | 1703 | 2713-XZY-00105 | SDO0001-01 | 2713-X-00105 | Z-00101 | 2713-XZY-00105 | Switch valve @ the recirculation line of styrene | Solenoid valve | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00101 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-D463/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2713-S-JB-D463 | SIS | 583 | BK | 02 |  | 1703 | 1340 |  | 2713-S-JB-D463 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 31 | DO32P
| 608 | 1703 | 2713-XZZSO-00105 | SDI0010-02R | 2713-X-00105 | - | 2713-XZZSO-00105 | Switch valve @ the recirculation line of styrene | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 07 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 10 | DI32
| 609 | 1703 | 2713-XZZSC-00105 | SDI0010-02R | 2713-X-00105 | - | 2713-XZZSC-00105 | Switch valve @ the recirculation line of styrene | Limit Switch | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 |  | 2713-S-JB-C457/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2713-S-JB-C457 | SIS | 583 | BU | 02 |  | 1703 | 1323 |  | 2713-S-JB-C457 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 11 | DI32
| 611 | 1703 | 2713-HZS-00101A-1 | SDI0010-01R | 2713-HZS-00101A | Z-00101 | 2713-HZS-00101A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00101 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 17 | DI32
| 612 | 1703 | 2713-HZS-00101B | SDI0010-01R | 2713-HZS-00101B | Z-00101 | 2713-HZS-00101B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00101 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-B477/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2713-S-JB-B477 | SIS |  | BK | 01 | Rev1 New add | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 2 | DI32
| 613 | 1703 | 2713-HZS-00701A-1 | SDI0010-01R | 2713-HZS-00701A | Z-00701 | 2713-HZS-00701A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00701 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 18 | DI32
| 614 | 1703 | 2713-HZS-00701B | SDI0010-01R | 2713-HZS-00701B | Z-00701 | 2713-HZS-00701B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00701 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-B477/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2713-S-JB-B477 | SIS |  | BK | 02 | Rev1 New add | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 3 | DI32
| 615 | 1703 | 2713-HZS-00702A-1 | SDI0010-01R | 2713-HZS-00702A | Z-00702 | 2713-HZS-00702A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00702 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 19 | DI32
| 616 | 1703 | 2713-HZS-00702B | SDI0010-01R | 2713-HZS-00702B | Z-00702 | 2713-HZS-00702B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00702 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-B477/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2713-S-JB-B477 | SIS |  | BK | 03 | Rev1 New add | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 4 | DI32
| 617 | 1703 | 2713-HZS-01001A-1 | SDI0010-01R | 2713-HZS-01001A | Z-01001 | 2713-HZS-01001A-1 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-01001 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 20 | DI32
| 618 | 1703 | 2713-HZS-01001B | SDI0010-01R | 2713-HZS-01001B | Z-01001 | 2713-HZS-01001B | Manual confirmation | PUSH BUTTION | 2000-S-SC-B01 | 2490156-1703-ST007-0000 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-01001 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-B477/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2713-S-JB-B477 | SIS |  | BK | 04 | Rev1 New add | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 5 | DI32
| 620 | 1703 | 2713-PZIA-00961 | SAI1000-01R | 2713-P-00961 | - | 2713-PZT-00961 | Seal auxiliary system of 2713-P-0002 | PRESSURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 0,3 | Mpag | - | - | - | - | - | 0,1 | - | Mpag | 1 | Rev1 Tag change | 2713-P-0002 | VINCI |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-C431/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2713-S-JB-C431 | SIS |  | BU |  | Rev1 new add for package | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 5 | AI16H
| 621 | 1703 | 2713-LZIA-00961 | SAI1000-01R | 2713-L-00961 | - | 2713-LZT-00961 | Seal auxiliary system of 2713-P-0002 | LEVEL TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | - | - | - | 0 | 400 | mmH2O | - | 64 | 281 | - | mmH2O | 1 | Rev1 Tag change | 2713-P-0002 | VINCI |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-C431/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2713-S-JB-C431 | SIS |  | BU |  | Rev1 new add for package | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 6 | AI16H
| 622 | 1703 | 2713-TZIA-00961 | SAI1000-01R | 2713-T-00961 | - | 2713-TZT-00961 | Bearing temperature of 2713-P-0002 | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 150 | ℃ | - | - | - | - | - | 85 | - | ℃ | 2 | Rev2 Change service Rev1 Tag change | 2713-P-0002 | VINCI |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-C431/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2713-S-JB-C431 | SIS |  | BU |  | Rev1 new add for package | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 7 | AI16H
| 623 | 1703 | 2713-PZIA-00962 | SAI1000-01R | 2713-P-00962 | - | 2713-PZT-00962 | Seal auxiliary system of 2713-P-0003 | PRESSURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 0,3 | Mpag | - | - | - | - | - | 0,1 | - | Mpag | 1 | Rev1 Tag change | 2713-P-0003 | VINCI |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-C432/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2713-S-JB-C431 | SIS |  | BU |  | Rev1 new add for package | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 8 | AI16H
| 624 | 1703 | 2713-LZIA-00962 | SAI1000-01R | 2713-L-00962 | - | 2713-LZT-00962 | Seal auxiliary system of 2713-P-0003 | LEVEL TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | - | - | - | 0 | 400 | mmH2O | - | 64 | 281 | - | mmH2O | 1 | Rev1 Tag change | 2713-P-0003 | VINCI |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-C432/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2713-S-JB-C431 | SIS |  | BU |  | Rev1 new add for package | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 9 | AI16H
| 625 | 1703 | 2713-TZIA-00962 | SAI1000-01R | 2713-T-00962 | - | 2713-TZT-00962 | Bearing temperature of 2713-P-0003 | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 150 | ℃ | - | - | - | - | - | 85 | - | ℃ | 2 | Rev2 Change service Rev1 Tag change | 2713-P-0003 | VINCI |  | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | 1 | 2713-S-JB-C432/SIS | 4x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 4x2x1.0 | 2713-S-JB-C431 | SIS |  | BU |  | Rev1 new add for package | 1703 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 10 | AI16H
| 627 | 1703 | 2713-MXI-00001A | SDO0001-01 | 2713-MXI-00001A | Z-00211/00212/00213/00311/00312/00313 | 2713-MXI-00001A | EB Loading Pump 2713-P-0001A Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00211/00212/00213/00311/00312/00313 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 13 | DO32P
| 628 | 1703 | 2713-MXI-10001A | SDO0001-01 | 2713-MXI-10001A | Z-00211/00212/00213/00311/00312/00313 | 2713-MXI-10001A | EB Loading Pump 2713-P-0001B Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00211/00212/00213/00311/00312/00313 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 14 | DO32P
| 629 | 1703 | 2713-MXI-00002A | SDO0001-01 | 2713-MXI-00002A | Z-00311/00313/00411/00413 | 2713-MXI-00002A | Drain Pump 2713-P-0002 Stop | Relay Contact(230VAC) | 3404-S-RC-P01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00311/00313/00411/00413 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [14 empty] | ? | 3404-S-RC-P01 | 3404-S-RC-P01 |  | A60 | A61 | 02 | 03 | A60-02 | A60-03 | A61-02 | A61-03 | 15 | DO32P
| 630 | 1703 | 2713-MXI-00003A | SDO0001-01 | 2713-MXI-00003A | Z-00312/00415 | 2713-MXI-00003A | Drain Pump 2713-P-0003 Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  | Z-00312/00415 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [14 empty] | ? | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 0 | DO32P
| 635 | 2311 | 2612-AZIA-04001 | SAI1000-01R | 2612-A-04001 | Z-23001 | 2612-AZT-04001 | PH Analyzer of Lp condensate | PH ANALYZER | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | AIR-LP | - | SIS | - | I | 0 | 14 | PH | 0 | 14 | PH | 8,5 | 8,6 | 9,4 | 9,5 | PH | 1 | Rev1 add range and alarm interlock set value, add signal isolator |  |  | Z-23001 | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | 1 | 2623-A-JB-B001/SIS | 4x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 4x2x1.0 | 2623-A-JB-B001（2612-ACU-401） | SIS | 590 | BK | 02 | Rev1 New add | 2311 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 13 | AI16H
| 636 | 2311 | 2612-AZIA-04001 | SAI1000-01R | 2612-A-04001 | - | 2612-AZIA-04001 | PH Analyzer of Lp condensate | Indicate & Control & Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 637 | 2311 | 2612-AZIA-04001 | SAI1000-01R | 2612-A-04001 | - | 2612-AZAHH-04001 | PH Analyzer of Lp condensate | Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 639 | 2311 | 2612-AZIA-04002 | SAI1000-01R | 2612-A-04002 | Z-23001 | 2612-AZT-04002 | Conductivity Analyzer of LC-Lp condensate | CONDUCTIVITY ANALYZER | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | AIR-LP | - | SIS | - | I | 1 | 20 | μs/cm | 1 | 20 | μs/cm | - | - | 4,6 | 5 | μs/cm | 1 | Rev1 add range and alarm interlock set value, add signal isolator |  |  | Z-23001 | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | 1 | 2623-A-JB-B001/SIS | 4x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 4x2x1.0 | 2623-A-JB-B001（2612-ACU-401） | SIS | 590 | BK | 03 | Rev1 New add | 2311 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 4 | AI16H
| 640 | 2311 | 2612-AZIA-04002 | SAI1000-01R | 2612-A-04002 | - | 2612-AZIA-04002 | Conductivity Analyzer of LC-Lp condensate | Indicate & Control & Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 641 | 2311 | 2612-AZIA-04002 | SAI1000-01R | 2612-A-04002 | - | 2612-AZAHH-04002 | Conductivity Analyzer of LC-Lp condensate | Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 643 | 2311 | 2612-AZIA-04003 | SAI1000-01R | 2612-A-04003 | Z-23001 | 2612-AZT-04003 | Total Organic Carbon Analyzer of Lp condensate | TOTAL ORGANIC CARBON ANALYZER | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | AIR-EP | - | SIS | - | I | 0 | 3000 | μg/L | 0 | 3000 | μg/L | - | - | 185 | 200 | μg/L | 1 | Rev1 add range and alarm interlock set value, add signal isolator |  |  | Z-23001 | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | 1 | 2623-A-JB-B011/SIS | 2x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 2x2x1.0 | 2623-A-JB-B011（2612-ACU-402） | SIS | 590 | BK | 01 | Rev1 New add | 2311 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 9 | AI16H
| 644 | 2311 | 2612-AZIA-04003 | SAI1000-01R | 2612-A-04003 | - | 2612-AZIA-04003 | Total Organic Carbon Analyzer of Lp condensate | Indicate & Control & Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 645 | 2311 | 2612-AZIA-04003 | SAI1000-01R | 2612-A-04003 | - | 2612-AZAHH-04003 | Total Organic Carbon Analyzer of Lp condensate | Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 647 | 2311 | 2612-AZIA-04004 | SAI1000-01R | 2612-A-04004 | Z-23001 | 2612-AZT-04004 | Silicon Dioxide Analyzer of Lp condensate | SILICON DIOXIDE ANALYZER | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | AIR-EP | - | SIS | - | I | 0 | 500 | μg/L | 0 | 500 | μg/L | - | - | 110 | 120 | μg/L | 1 | Rev1 add range and alarm interlock set value, add signal isolator |  |  | Z-23001 | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | 1 | 2623-A-JB-B021/SIS | 2x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 2x2x1.0 | 2623-A-JB-B021（2612-ACU-403） | SIS | 590 | BK | 01 | Rev1 New add | 2311 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 10 | AI16H
| 648 | 2311 | 2612-AZIA-04004 | SAI1000-01R | 2612-A-04004 | - | 2612-AZIA-04004 | Silicon Dioxide Analyzer of Lp condensate | Indicate & Control & Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 649 | 2311 | 2612-AZIA-04004 | SAI1000-01R | 2612-A-04004 | - | 2612-AZAHH-04004 | Silicon Dioxide Analyzer of Lp condensate | Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 651 | 2311 | 2612-AZIA-04005 | SAI1000-01R | 2612-A-04005 | Z-23001 | 2612-AZT-04005 | Oil In Water Analyzer of Lp condensate | OIL IN WATER ANALYZER | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | AIR-EP | - | SIS | - | I | 0 | 10 | mg/L | 0 | 10 | mg/L | - | - | 0,45 | 0,5 | mg/L | 1 | Rev1 add range and alarm interlock set value, add signal isolator |  |  | Z-23001 | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | 1 | 2623-A-JB-B001/SIS | 4x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 4x2x1.0 | 2623-A-JB-B001（2612-ACU-401） | SIS | 590 | BK | 01 | Rev1 New add | 2311 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 8 | AI16H
| 652 | 2311 | 2612-AZIA-04005 | SAI1000-01R | 2612-A-04005 | - | 2612-AZIA-04005 | Oil In Water Analyzer of Lp condensate | Indicate & Control & Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 653 | 2311 | 2612-AZIA-04005 | SAI1000-01R | 2612-A-04005 | - | 2612-AZAHH-04005 | Oil In Water Analyzer of Lp condensate | Alarm:SIS | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 655 | 2311 | 2612-XZY-04001 | SDO0001-01 | 2612-X-04001 | - | 2612-XZV-04001 | Switch Valve @ LC-Lp condensate | ON-OFF BALL VALVE | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 656 | 2311 | 2612-XZY-04001 | SDO0001-01 | 2612-X-04001 | Z-23001 | 2612-XZY-04001 | Switch Valve @ LC-Lp condensate | Solenoid valve | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | DOR-P | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-23001 | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 |  | 2623-S-JB-D606/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2623-S-JB-D606 | SIS | 575 | BK | 01 |  | 2311 | 1571 |  | 2623-S-JB-D606 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 1 | DO32P
| 657 | 2311 | 2612-XZZSC-04001 | SDI0010-02R | 2612-X-04001 | - | 2612-XZZSC-04001 | Switch Valve @ LC-Lp condensate | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | DIR-NAMUR | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 |  | 2623-S-JB-B605/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2623-S-JB-B605 | SIS | 575 | BK | 01 |  | 2311 | 1562 |  | 2623-S-JB-B605 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 24 | DI32
| 658 | 2311 | 2612-XZZSO-04001 | SDI0010-02R | 2612-X-04001 | - | 2612-XZZSO-04001 | Switch Valve @ LC-Lp condensate | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | DIR-NAMUR | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 |  | 2623-S-JB-B605/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2623-S-JB-B605 | SIS | 575 | BK | 03 |  | 2311 | 1562 |  | 2623-S-JB-B605 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 26 | DI32
| 660 | 2311 | 2612-XZY-04002 | SDO0001-01 | 2612-X-04002 | - | 2612-XZV-04002 | Switch Valve @ LC-Lp condensate | ON-OFF BALL VALVE | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版
| 661 | 2311 | 2612-XZY-04002 | SDO0001-01 | 2612-X-04002 | Z-23001 | 2612-XZY-04002 | Switch Valve @ LC-Lp condensate | Solenoid valve | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | DOR-P | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-23001 | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 |  | 2623-S-JB-D606/SIS | 16x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-KYJVP3 16x2.5mm2 | 2623-S-JB-D606 | SIS | 575 | BK | 02 |  | 2311 | 1571 |  | 2623-S-JB-D606 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 2 | DO32P
| 662 | 2311 | 2612-XZZSC-04002 | SDI0010-02R | 2612-X-04002 | - | 2612-XZZSC-04002 | Switch Valve @ LC-Lp condensate | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | DIR-NAMUR | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 |  | 2623-S-JB-B605/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2623-S-JB-B605 | SIS | 575 | BK | 02 |  | 2311 | 1562 |  | 2623-S-JB-B605 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 25 | DI32
| 663 | 2311 | 2612-XZZSO-04002 | SDI0010-02R | 2612-X-04002 | - | 2612-XZZSO-04002 | Switch Valve @ LC-Lp condensate | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-2311-TS007-0004 | Field | DIR-NAMUR | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 |  | 2623-S-JB-B605/SIS | 8x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2623-S-JB-B605 | SIS | 575 | BK | 04 |  | 2311 | 1562 |  | 2623-S-JB-B605 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 27 | DI32
| 665 | 2311 | 2623-TZIA-23101A | SAI1000-01R | 2623-T-23101A | Z-03001A | 2623-TZT-23101A | Temperature Transmitter For Pump Bearing | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | NKNH21002-2311-PO0009-121-0001 | Field | AIR-LP | - | SIS | - | - | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 90 | 95 | ℃ | 2 | Rev2 change Tag No. | 2623-P-3001A | SDPump |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 5 | AI16H
| 666 | 2311 | 2623-TZIA-23101B | SAI1000-01R | 2623-T-23101B | Z-03001B | 2623-TZT-23101B | Temperature Transmitter For Pump Bearing | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | NKNH21002-2311-PO0009-121-0002 | Field | AIR-LP | - | SIS | - | - | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 90 | 95 | ℃ | 2 | Rev2 change Tag No. | 2623-P-3001B | SDPump |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 6 | AI16H
| 667 | 2311 | 2623-TZIA-23101C | SAI1000-01R | 2623-T-23101C | Z-03001C | 2623-TZT-23101C | Temperature Transmitter For Pump Bearing | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | NKNH21002-2311-PO0009-121-0003 | Field | AIR-LP | - | SIS | - | - | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 90 | 95 | ℃ | 2 | Rev2 change Tag No. | 2623-P-3001C | SDPump |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 7 | AI16H
| 668 | 2311 | 2612-TZIA-23302A | SAI1000-01R | 2623-T-23302A | Z-03003A | 2612-TZT-23302A | Temperature Transmitter For Pump Bearing | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | NKNH21002-2311-PO0009-121-0004 | Field | AIR-LP | - | SIS | - | - | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 90 | 95 | ℃ | 2 | Rev2 change Tag No. | 2623-P-3003A | SDPump |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 8 | AI16H
| 669 | 2311 | 2612-TZIA-23302B | SAI1000-01R | 2623-T-23302B | Z-03003B | 2612-TZT-23302B | Temperature Transmitter For Pump Bearing | TEMPERATURE TRANSMITTER | 2000-S-SC-B01 | NKNH21002-2311-PO0009-121-0005 | Field | AIR-LP | - | SIS | - | - | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 90 | 95 | ℃ | 2 | Rev2 change Tag No. | 2623-P-3003B | SDPump |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 9 | AI16H
| 678 | 2311 | 2623-MXI-03001A | SDO0001-01 | 2623-MXI-03001A | Z-03001A | 2623-MXI-03001A | 2623-P-3001A Emergency stop | Relay contact | 2000-S-SC-B01 | 2490156-2311-TS007-0000F | 2203 | DOR-P | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 07 | 08 | A13-07 | A13-08 | A14-07 | A14-08 | 0 | DO32P
| 679 | 2311 | 2623-MXI-13001A | SDO0001-01 | 2623-MXI-13001A | Z-03001B | 2623-MXI-13001A | 2623-P-3001B Emergency stop | Relay contact | 2000-S-SC-B01 | 2490156-2311-TS007-0000F | 2203 | DOR-P | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 07 | 08 | A13-07 | A13-08 | A14-07 | A14-08 | 2 | DO32P
| 680 | 2311 | 2623-MXI-23001A | SDO0001-01 | 2623-MXI-23001A | Z-03001C | 2623-MXI-23001A | 2623-P-3001C Emergency stop | Relay contact | 2000-S-SC-B01 | 2490156-2311-TS007-0000F | 2203 | DOR-P | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 07 | 08 | A13-07 | A13-08 | A14-07 | A14-08 | 4 | DO32P
| 682 | 2311 | 2623-MXI-03003A | SDO0001-01 | 2623-MXI-03003A | Z-03003A | 2623-MXI-03003A | 2623-P-3003A Emergency stop | Relay contact | 2000-S-SC-B01 | 2490156-2311-TS007-0000F | 2203 | DOR-P | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 07 | 08 | A13-07 | A13-08 | A14-07 | A14-08 | 1 | DO32P
| 683 | 2311 | 2623-MXI-13003A | SDO0001-01 | 2623-MXI-13003A | Z-03003B | 2623-MXI-13003A | 2623-P-3003B Emergency stop | Relay contact | 2000-S-SC-B01 | 2490156-2311-TS007-0000F | 2203 | DOR-P | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  |  | G3 NKNH21002-2311-ATX.LST-0004_3_EN 待出版 | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 07 | 08 | A13-07 | A13-08 | A14-07 | A14-08 | 3 | DO32P
| 685 | 2818 | 2650-PZIA-20003 | SAI1000-01R | 2650-P(S)-003 | Z-10001 | 2650-PZT-20003 | Discharge Pressure of Screw Compressor | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0003 | Field | AIR-LP | Ex.i | SIS | - | B | -0,1 | 2,4 | Mpag | -0,1 | 2,4 | Mpag | - | - | 1,37 | 1,43 | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C691/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C691 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 8 | AI16H
| 686 | 2818 | 2650-PZIA-20004 | SAI1000-01R | 2650-P(S)-004 | Z-10001 | 2650-PZT-20004 | Discharge Pressure of Screw Compressor | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0003 | Field | AIR-LP | Ex.i | SIS | - | B | -0,1 | 2,4 | Mpag | -0,1 | 2,4 | Mpag | - | - | 1,37 | 1,43 | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C691/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C691 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 8 | AI16H
| 687 | 2818 | 2650-PZIA-20005A | SAI1000-01R | 2650-P(S)-005A | Z-10001 | 2650-PZT-20005A | Oil Supply Pressure of Screw Compressor A | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0002 | Field | AIR-LP | Ex.i | SIS | - | - | -0,1 | 2,4 | Mpag | -0,1 | 2,4 | Mpag | - | - | - | - | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C675/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C675 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 9 | AI16H
| 688 | 2818 | 2650-PZT-20006A | SAI1000-01R | 2650-P(S)-006A | Z-10001 | 2650-PZT-20006A | Oil Supply Pressure of Screw Compressor A | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0002 | Field | AIR-LP | Ex.i | SIS | - | - | -0,1 | 2,4 | Mpag | -0,1 | 2,4 | Mpag | - | - | - | - | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C675/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C675 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 12 | AI16H
| 689 | 2818 | 2650-PDZY-20005A | AI1000-01 | 2650-PD(S)-005A | Z-10001 | 2650-PDZY-20005A | Oil Supply Differential Pressure(2650-PI-20005A minus 2650-PI-20003) | - | 2000-S-SC-B01 | - | SIS | S | - | SIS | - | - | - | - | - | - | - | - | 0,15 | 0,17 | - | - | MPa | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 690 | 2818 | 2650-PDZY-20006A | AI1000-01R | 2650-PD(S)-006A | Z-10001 | 2650-PDZY-20006A | Oil Supply Differential Pressure(2650-PI-20006A minus 2650-PI-20004) | - | 2000-S-SC-B01 | - | SIS | S | - | SIS | - | - | - | - | - | - | - | - | 0,15 | 0,17 | - | - | MPa | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 691 | 2818 | 2650-PZIA-20005B | SAI1000-01R | 2650-P(S)-005B | Z-10001 | 2650-PZT-20005B | Oil Supply Pressure of Screw Compressor B | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0002 | Field | AIR-LP | Ex.i | SIS | - | - | -0,1 | 2,4 | Mpag | -0,1 | 2,4 | Mpag | - | - | - | - | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C675/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C675 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 9 | AI16H
| 692 | 2818 | 2650-PZIA-20006B | SAI1000-01R | 2650-P(S)-006B | Z-10001 | 2650-PZT-20006B | Oil Supply Pressure of Screw Compressor B | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0002 | Field | AIR-LP | Ex.i | SIS | - | - | -0,1 | 2,4 | Mpag | -0,1 | 2,4 | Mpag | - | - | - | - | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C675/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C675 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 0 | AI16H
| 693 | 2818 | 2650-PDZY-20005B | AI1000-01 | 2650-PD(S)-005B | Z-10001 | 2650-PDZY-20005B | Oil Supply Differential Pressure(2650-PI-20005B minus 2650-PI-20003) | - | 2000-S-SC-B01 | - | SIS | S | - | SIS | - | - | - | - | - | - | - | - | 0,15 | 0,17 | - | - | MPa | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 694 | 2818 | 2650-PDZY-20006B | AI1000-01 | 2650-PD(S)-006B | Z-10001 | 2650-PDZY-20006B | Oil Supply Differential Pressure(2650-PI-20006B minus 2650-PI-20004) | - | 2000-S-SC-B01 | - | SIS | S | - | SIS | - | - | - | - | - | - | - | - | 0,15 | 0,17 | - | - | MPa | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 695 | 2818 | 2650-PZIA-20013 | SAI1000-01R | 2650-P(S)-013 | Z-10001 | 2650-PZT-20013 | Lube Oil Supply Pressure | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0007 | Field | AIR-LP | Ex.i | SIS | - | B | 0 | 1,6 | Mpag | 0 | 1,6 | Mpag | 0,04 | 0,045 | - | - | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C691/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C691 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 10 | AI16H
| 696 | 2818 | 2650-PZIA-20014 | SAI1000-01R | 2650-P(S)-014 | Z-10001 | 2650-PZT-20014 | Lube Oil Supply Pressure | Pressure Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0007 | Field | AIR-LP | Ex.i | SIS | - | B | 0 | 1,6 | Mpag | 0 | 1,6 | Mpag | 0,04 | 0,045 | - | - | Mpag | 2 | Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C691/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C691 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 1 | AI16H
| 697 | 2818 | 2650-PZIA-20104 | SAI1000-01R | 2650-T(S)-004 | Z-10001 | 2650-TZT-20104 | Oil Supply Temperature | Temperature Sensor & Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0003 | Field | AIR-LP | Ex.i | SIS | - | B | -50 | 200 | degC | -50 | 200 | degC | - | - | 63 | 65 | degC | 3 | Rev3 Change Tag No. Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C691/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C691 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 10 | AI16H
| 698 | 2818 | 2650-PZIA-20105 | SAI1000-01R | 2650-T(S)-005 | Z-10001 | 2650-TZT-20105 | Oil Supply Temperature | Temperature Sensor & Transmitter | 2000-S-SC-B01 | NKNH21002-2000-PO0010-121-0003 | Field | AIR-LP | Ex.i | SIS | - | B | -50 | 200 | degC | -50 | 200 | degC | - | - | 63 | 65 | degC | 3 | Rev3 Change Tag No. Rev2 New add | 2650-PK-1001 |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C691/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C691 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 11 | AI16H
| 699 | 2818 | 2602-XZY-00203 | SDO0001-01 | 2602-X-00203 | - | 2602-XZV-00203 | Emergency nitrogen supply shut-off valve | ON-OFF BALL VALVE | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 700 | 2818 | 2602-XZY-00203 | SDO0001-01 | 2602-X-00203 | Z-00001 | 2602-XZY-00203 | Emergency nitrogen supply shut-off valve | Solenoid valve | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN |  | 2602-XZY-00203/SIS | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 2x2.5mm2 | 2602-XZY-00203 | SIS | 620 | BK |  |  | 2818 |  |  | SIS |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 0 | DO32P
| 701 | 2818 | 2602-XZZSC-00203 | SDI0010-02R | 2602-X-00203 | - | 2602-XZZSC-00203 | Emergency nitrogen supply shut-off valve | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN |  | 2650-S-JB-C682/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C682 | SIS | 606 | BU | 01 |  | 2818 | 1641 |  | 2650-S-JB-C682 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 0 | DI32
| 702 | 2818 | 2602-XZZSO-00203 | SDI0010-02R | 2602-X-00203 | - | 2602-XZZSO-00203 | Emergency nitrogen supply shut-off valve | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN |  | 2650-S-JB-C682/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C682 | SIS | 606 | BU | 02 |  | 2818 | 1641 |  | 2650-S-JB-C682 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 1 | DI32
| 704 | 2818 | 2120-XZY-00204 | SDO0001-01 | 2120-X-00204 | - | 2120-XZV-00204 | Propane from battery limit | ON-OFF BALL VALVE | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | - | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 705 | 2818 | 2120-XZY-00204 | SDO0001-01 | 2120-X-00204 | - | 2120-XZY-00204 | Propane from battery limit | Solenoid valve | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2120-XZY-00204/SIS | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 2x2.5mm2 | 2120-XZY-00204 | SIS | 630 | BK |  | Rev1 New add | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 4 | DO32P
| 706 | 2818 | 2120-XZZSC-00204 | SDI0010-02R | 2120-X-00204 | - | 2120-XZZSC-00204 | Propane from battery limit | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C682/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C682 | SIS | 606 | BU | 03 | Rev1 New add | 2818 | 1641 |  | 2650-S-JB-C682 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 12 | DI32
| 707 | 2818 | 2120-XZZSO-00204 | SDI0010-02R | 2120-X-00204 | - | 2120-XZZSO-00204 | Propane from battery limit | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 2 | Rev2 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C682/SIS | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 8x2x1.0 | 2650-S-JB-C682 | SIS | 606 | BU | 04 | Rev1 New add | 2818 | 1641 |  | 2650-S-JB-C682 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 13 | DI32
| 709 | 2818 | 2603-FZIA-00201 | SAI1000-01R | 2603-F-00201 | Z-00001 | 2603-FZT-00201 | Fuel gas flow meter | Integral Orifice Plate | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 25 | kPa | 0 | 25 | kPa | - | - | - | - | - | 0 | - |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN |  | 2603-FZT-00201/SIS | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | NH-IA-DJYVP3 1x2x1.5 | 2603-FZT-00201 | SIS | 620 | BU |  |  | 2818 |  |  | SIS |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 0 | AI16H
| 710 | 2818 | 2603-FZIA-00201 | SAI1000-01R | 2603-F-00201 | - | 2603-FZIA-00201 | Fuel gas flow meter | Indicate:SIS | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 711 | 2818 | 2603-FZIA-00201 | SAI1000-01R | 2603-F-00201 | - | 2603-FALL-00201 | Fuel gas flow meter | Alarm:SIS | 2000-S-SC-B01 | 2490156-2818-AR007-0002 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_3_EN
| 713 | 2818 | 2650-TZIA-20001A | SAI1000-01R | 2650-T-20001A | Z-P1001A | 2650-TZT-20001A | Temperature of Motor bearing NDEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 0 | AI16H
| 714 | 2818 | 2650-TZIA-20002A | SAI1000-01R | 2650-T-20002A | Z-P1001A | 2650-TZT-20002A | Temperature of Motor bearing NDEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 0 | AI16H
| 715 | 2818 | 2650-TZIA-20009A | SAI1000-01R | 2650-T-20009A | Z-P1001A | 2650-TZT-20009A | Temperature of motor bearing DEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 1 | AI16H
| 716 | 2818 | 2650-TZIA-20010A | SAI1000-01R | 2650-T-20010A | Z-P1001A | 2650-TZT-20010A | Temperature of motor bearing DEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 1 | AI16H
| 717 | 2818 | 2650-TZIA-20011A | SAI1000-01R | 2650-T-20011A | Z-P1001A | 2650-TZT-20011A | Temperature of pump bearing DEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 2 | AI16H
| 718 | 2818 | 2650-TZIA-20012A | SAI1000-01R | 2650-T-20012A | Z-P1001A | 2650-TZT-20012A | Temperature of pump bearing DEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 2 | AI16H
| 719 | 2818 | 2650-TZIA-20013A | SAI1000-01R | 2650-T-20013A | Z-P1001A | 2650-TZT-20013A | Temperature of pump bearing NDEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 3 | AI16H
| 720 | 2818 | 2650-TZIA-20014A | SAI1000-01R | 2650-T-20014A | Z-P1001A | 2650-TZT-20014A | Temperature of pump bearing NDEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001A | SDPump | Z-P1001A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C660/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C660 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 3 | AI16H
| 721 | 2818 | 2650-TZIA-20001B | SAI1000-01R | 2650-T-20001B | Z-P1001B | 2650-TZT-20001B | Temperature of Motor bearing NDEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 4 | AI16H
| 722 | 2818 | 2650-TZIA-20002B | SAI1000-01R | 2650-T-20002B | Z-P1001B | 2650-TZT-20002B | Temperature of Motor bearing NDEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 4 | AI16H
| 723 | 2818 | 2650-TZIA-20009B | SAI1000-01R | 2650-T-20009B | Z-P1001B | 2650-TZT-20009B | Temperature of motor bearing DEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 5 | AI16H
| 724 | 2818 | 2650-TZIA-20010B | SAI1000-01R | 2650-T-20010B | Z-P1001B | 2650-TZT-20010B | Temperature of motor bearing DEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 100 | ℃ | 0 | 100 | ℃ | - | - | 90 | 95 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 5 | AI16H
| 725 | 2818 | 2650-TZIA-20011B | SAI1000-01R | 2650-T-20011B | Z-P1001B | 2650-TZT-20011B | Temperature of pump bearing DEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 6 | AI16H
| 726 | 2818 | 2650-TZIA-20012B | SAI1000-01R | 2650-T-20012B | Z-P1001B | 2650-TZT-20012B | Temperature of pump bearing DEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 6 | AI16H
| 727 | 2818 | 2650-TZIA-20013B | SAI1000-01R | 2650-T-20013B | Z-P1001B | 2650-TZT-20013B | Temperature of pump bearing NDEX | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 7 | AI16H
| 728 | 2818 | 2650-TZIA-20014B | SAI1000-01R | 2650-T-20014B | Z-P1001B | 2650-TZT-20014B | Temperature of pump bearing NDEY | Temperature Transmitter | 2000-S-SC-B01 | - | Field | AIR(I)-LP | Ex.i | SIS | - | B | -50 | 150 | ℃ | -50 | 150 | ℃ | - | - | 80 | 90 | ℃ | 1 | Rev1 Move from DCS | 2650-P-1001B | SDPump | Z-P1001B | H3 NKNH21002-2818-ATX.LST-0004_3_EN | 1 | 2650-S-JB-C663/SIS | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 12x2x1.0 | 2650-S-JB-C663 | SIS |  | BU |  | Rev1 add for package | 2818 |  |  |  |  | 2000-S-SC-B01 | 2000-S-MC-B02F |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 7 | AI16H
| 731 | 2818 | 2650-MXI-01001A | SDO0001-01 | 2650-MXI-01001A | Z-P1001A/10004 | 2650-MXI-01001A | Chilled Water Pump 2650-P-1001A Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 1 | DO32P
| 732 | 2818 | 2650-MXI-11001A | SDO0001-01 | 2650-MXI-11001A | Z-P1001B/10004 | 2650-MXI-11001A | Chilled Water Pump 2650-P-1001B Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 2 | DO32P
| 733 | 2818 | 2650-MXI-02001A | SDO0001-01 | 2650-MXI-02001A | Z-10001/10004/10005 | 2650-MXI-02001A | Refrigerator Compressor 2650-K-2001A Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 3 | DO32P
| 734 | 2818 | 2650-MXI-12001A | SDO0001-01 | 2650-MXI-12001A | Z-10001/10004/10005 | 2650-MXI-12001A | Refrigerator Compressor 2650-K-2001B Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 4 | DO32P
| 735 | 2818 | 2650-MXI-22001A | SDO0001-01 | 2650-MXI-22001A | Z-10001/10004/10005 | 2650-MXI-22001A | Oil Pump 2650-P-2001A Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 5 | DO32P
| 736 | 2818 | 2650-MXI-32001A | SDO0001-01 | 2650-MXI-32001A | Z-10001/10004/10005 | 2650-MXI-32001A | Oil Pump 2650-P-2001B Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 6 | DO32P
| 737 | 2818 | 2650-MXI-02002A | SDO0001-01 | 2650-MXI-02002A | Z-10004 | 2650-MXI-02002A | Accident Ventilation Fan 2650-BL-2002A Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 7 | DO32P
| 738 | 2818 | 2650-MXI-12002A | SDO0001-01 | 2650-MXI-12002A | Z-10004 | 2650-MXI-12002A | Accident Ventilation Fan 2650-BL-2002B Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 8 | DO32P
| 739 | 2818 | 2650-MXI-02002B | SDO0001-01 | 2650-MXI-02002B | Z-10005 | 2650-MXI-02002B | Accident Ventilation Fan 2650-BL-2002A Start | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 9 | DO32P
| 740 | 2818 | 2650-MXI-12002B | SDO0001-01 | 2650-MXI-12002B | Z-10005 | 2650-MXI-12002B | Accident Ventilation Fan 2650-BL-2002B Start | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-00001 | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 10 | DO32P
| 742 | 2818 | 2650-GZY-00001 | SDI0010-01R | 2650-GZY-00001 | Z-10004 | 2650-GZY-00001 | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-10004A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 6 | DI32
| 743 | 2818 | 2650-GZY-00002 | SDI0010-01R | 2650-GZY-00002 | Z-10005 | 2650-GZY-00002 | GDS Interlock to SIS | Relay Contact | 2000-S-SC-B01 | - | GDS | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 3 | Rev3 New add |  |  | Z-10004A | H3 NKNH21002-2818-ATX.LST-0004_3_EN | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B04F |  | A13 | A14 | 01 | - | A13-01 | - | A14-01 | - | 7 | DI32
Изм 2026.06.19 New | 745 | 005 | 0005-HZS-10006-1 | SDI0010-01R | - | 0005-Z-1006/2622-I-00001 | 0005-HZS-10006-1 | Title 2307 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 1 | DI32
Изм 2026.06.19 New | 746 | 005 | 0005-HZS-10008-1 | SDI0010-01R | - | 2711-Z-10001 | 0005-HZS-10008-1 | Title 1402 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 2 | DI32
Изм 2026.06.19 New | 747 | 005 | 0005-HZS-10009-1 | SDI0010-01R | - | 2818-Z-00002 | 0005-HZS-10009-1 | Title 2818 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 3 | DI32
Изм 2026.06.19 New | 748 | 005 | 0005-HZS-10010-1 | SDI0010-01R | - | 2311-I-07001 | 0005-HZS-10010-1 | Title 2311 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 4 | DI32
Изм 2026.06.19 New | 749 | 005 | 0005-HZS-10011-1 | SDI0010-01R | - | 2712-Z-10001 | 0005-HZS-10011-1 | Title 1702 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 5 | DI32
Изм 2026.06.19 New | 750 | 005 | 0005-HZS-10012-1 | SDI0010-01R | - | 2713-Z-10001 | 0005-HZS-10012-1 | Title 1703 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 6 | DI32
Изм 2026.06.19 New | 751 | 005 | 0005-HZS-10013-1 | SDI0010-01R | - | 2630-I-26001 | 0005-HZS-10013-1 | Title 2304 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 7 | DI32
Изм 2026.06.19 New | 752 | 2306 | 0005-DZY-10006 | SDO0001-01 | - | 0005-Z-1006/2622-I-00001 | 0005-DZY-10006 | SIS Interlock to DCS | Relay Contact | 2000-S-SC-B01 | - | DCS | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 8 | DO32P
Изм 2026.06.19 New | 753 | 2311 | 0005-DZY-10010 | SDO0001-01 | - | 0005-Z-1010/2311-I-07001 | 0005-DZY-10010 | SIS Interlock to DCS | Relay Contact | 2000-S-SC-B01 | - | DCS | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 9 | DO32P
Изм 2026.06.19 New | 754 | 2304 | 0005-DZY-10013 | SDO0001-01 | - | 0005-Z-1013/2630-I-26001 | 0005-DZY-10013 | SIS Interlock to DCS | Relay Contact | 2000-S-SC-B01 | - | DCS | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 10 | DO32P
Изм 2026.06.19 New | 755 | 2000 | 2000-MOS-10001-1 | SDI0010-01R | - | - | 2000-MOS-10001-1 | OSBL MOS Enabled | Switch | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 8 | DI32
Изм 2026.06.19 New | 756 | 2000 | 2000-MOS-10002 | SDO0001-01 | - | - | 2000-MOS-10002 | OSBL MOS Enabled | Light(Yellow) | 0000-S-RC-C03 | - | AUX | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 05 | 06 | A205-05 | A205-06 | A206-05 | A206-06 | 0 | DO32P
Изм 2026.06.19 New | 757 | 2000 | 2000-MOS-10003 | SDO0001-01 | - | - | 2000-MOS-10003 | OSBL MOS Timeout | Light(Red) | 0000-S-RC-C03 | - | AUX | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 05 | 06 | A205-05 | A205-06 | A206-05 | A206-06 | 1 | DO32P
Изм 2026.06.19 New | 762 | 2818 | 2650-MXI-22002A | SDO0001-01 | - | Z-10004 | 2650-MXI-22002A | Lube Oil Pump 2650-P-2002A Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_4_EN Update | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 12 | DO32P
Изм 2026.06.19 New | 763 | 2818 | 2650-MXI-32002A | SDO0001-01 | - | Z-10004 | 2650-MXI-32002A | Lube Oil Pump 2650-P-2002B Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_4_EN Update | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 13 | DO32P
Изм 2026.06.19 New | 764 | 2818 | 2650-MXI-42001A | SDO0001-01 | - | Z-10004 | 2650-MXI-42001A | Ventilation Fan 2650-BL-2001A Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_4_EN Update | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 14 | DO32P
Изм 2026.06.19 New | 765 | 2818 | 2650-MXI-52001A | SDO0001-01 | - | Z-10004 | 2650-MXI-52001A | Ventilation Fan 2650-BL-2001B Stop | Relay Contact(230VAC) | 2203-S-RC-S01 | - | MCC | DOR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | H3 NKNH21002-2818-ATX.LST-0004_4_EN Update | [15 empty] | 2203-S-RC-S01 | 2203-S-RC-S01 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 15 | DO32P
Изм 2026.06.19 Change tag 2701-HZS-10007 -> 0005-HZS-10007 | 766 | 005 | 0005-HZS-10007-2 | SDI0010-01R | 0005-HZS-10007 | 2701-Z-10004 | 0005-HZS-10007-2 | Process block interlock (ESD-2) | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1401-PR007-0101A | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change tag no |  |  | Z-10004 | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 0 | DI32
| 767 | 1402 | 2711-HZS-00107A-2 | SDI0010-01R | 2711-HS-00107A | 2711-Z-00107 | 2711-HZS-00107A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001A | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00107 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 9 | DI32
| 768 | 1402 | 2711-HZS-00108A-2 | SDI0010-01R | 2711-HS-00108A | 2711-Z-00108 | 2711-HZS-00108A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001B | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00108 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 10 | DI32
| 769 | 1402 | 2711-HZS-00109A-2 | SDI0010-01R | 2711-HS-00109A | 2711-Z-00109 | 2711-HZS-00109A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001C | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00109 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 11 | DI32
| 770 | 1402 | 2711-HZS-00401A-2 | SDI0010-01R | 2711-HS-00401A | 2711-Z-00403 | 2711-HZS-00401A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0004 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00403 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 12 | DI32
| 771 | 1402 | 2711-HZS-00501A-2 | SDI0010-01R | 2711-HS-00501A | 2711-Z-00503 | 2711-HZS-00501A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0005 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00503 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 13 | DI32
| 772 | 1402 | 2711-HZS-00601A-2 | SDI0010-01R | 2711-HS-00601A | 2711-Z-00603 | 2711-HZS-00601A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0006 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev3 change Tag No. Rev1 change Tag No. |  |  | Z-00603 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 14 | DI32
| 773 | 1702 | 2712-HZS-00101A-2 | SDI0010-01R | 2712-HZS-00101A | Z-00101 | 2712-HZS-00101A-2 | Emergency Shutdown Pushbutton | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1702-ST007-0001 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00101 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 15 | DI32
| 774 | 1702 | 2712-HZS-00102A-2 | SDI0010-01R | 2712-HZS-00102A | Z-00102 | 2712-HZS-00102A-2 | Emergency Shutdown Pushbutton | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1702-ST007-0001 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 16 | DI32
| 775 | 1703 | 2713-HZS-00101A-2 | SDI0010-01R | 2713-HZS-00101A | Z-00101 | 2713-HZS-00101A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00101 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 17 | DI32
| 776 | 1703 | 2713-HZS-00701A-2 | SDI0010-01R | 2713-HZS-00701A | Z-00701 | 2713-HZS-00701A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00701 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 18 | DI32
| 777 | 1703 | 2713-HZS-00702A-2 | SDI0010-01R | 2713-HZS-00702A | Z-00702 | 2713-HZS-00702A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00702 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 19 | DI32
| 778 | 1703 | 2713-HZS-01001A-1 | SDI0010-01R | 2713-HZS-01001A | Z-01001 | 2713-HZS-01001A-2 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-01001 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 20 | DI32
Изм 2026.06.19 New | 779 | 005 | 0005-HZS-10006-2 | SDI0010-01R | - | 0005-Z-1006/2622-I-00001 | 0005-HZS-10006-2 | Title 2307 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 1 | DI32
Изм 2026.06.19 New | 780 | 005 | 0005-HZS-10008-2 | SDI0010-01R | - | 2711-Z-10001 | 0005-HZS-10008-2 | Title 1402 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 2 | DI32
Изм 2026.06.19 New | 781 | 005 | 0005-HZS-10009-2 | SDI0010-01R | - | 2818-Z-00002 | 0005-HZS-10009-2 | Title 2818 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 3 | DI32
Изм 2026.06.19 New | 782 | 005 | 0005-HZS-10010-2 | SDI0010-01R | - | 2311-I-07001 | 0005-HZS-10010-2 | Title 2311 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 4 | DI32
Изм 2026.06.19 New | 783 | 005 | 0005-HZS-10011-2 | SDI0010-01R | - | 2712-Z-10001 | 0005-HZS-10011-2 | Title 1702 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 5 | DI32
Изм 2026.06.19 New | 784 | 005 | 0005-HZS-10012-2 | SDI0010-01R | - | 2713-Z-10001 | 0005-HZS-10012-2 | Title 1703 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 6 | DI32
Изм 2026.06.19 New | 785 | 005 | 0005-HZS-10013-2 | SDI0010-01R | - | 2630-I-26001 | 0005-HZS-10013-2 | Title 2304 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 7 | DI32
Изм 2026.06.19 New | 786 | 2000 | 2000-MOS-10001-2 | SDI0010-01R | - | - | 2000-MOS-10001-2 | OSBL MOS Enabled | Switch | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 03 | - | A205-03 | - | A206-03 | - | 8 | DI32
Изм 2026.06.19 Change tag 2701-HZS-10007 -> 0005-HZS-10007 | 787 | 005 | 0005-HZS-10007-3 | SDI0010-01R | 0005-HZS-10007 | 2701-Z-10004 | 0005-HZS-10007-3 | Process block interlock (ESD-2) | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1401-PR007-0101A | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change tag no |  |  | Z-10004 | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 0 | DI32
| 788 | 1402 | 2711-HZS-00107A-3 | SDI0010-01R | 2711-HS-00107A | 2711-Z-00107 | 2711-HZS-00107A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001A | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00107 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 9 | DI32
| 789 | 1402 | 2711-HZS-00108A-3 | SDI0010-01R | 2711-HS-00108A | 2711-Z-00108 | 2711-HZS-00108A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001B | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00108 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 10 | DI32
| 790 | 1402 | 2711-HZS-00109A-3 | SDI0010-01R | 2711-HS-00109A | 2711-Z-00109 | 2711-HZS-00109A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0001C | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00109 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 11 | DI32
| 791 | 1402 | 2711-HZS-00401A-3 | SDI0010-01R | 2711-HS-00401A | 2711-Z-00403 | 2711-HZS-00401A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0004 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00403 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 12 | DI32
| 792 | 1402 | 2711-HZS-00501A-3 | SDI0010-01R | 2711-HS-00501A | 2711-Z-00503 | 2711-HZS-00501A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0005 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 change Tag No. |  |  | Z-00503 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 13 | DI32
| 793 | 1402 | 2711-HZS-00601A-3 | SDI0010-01R | 2711-HS-00601A | 2711-Z-00603 | 2711-HZS-00601A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1402-ST007-0006 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev3 change Tag No. Rev1 change Tag No. |  |  | Z-00603 | C3 NKNH21002-1402-ATX.LST-0004_3_EN. 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 14 | DI32
| 794 | 1702 | 2712-HZS-00101A-3 | SDI0010-01R | 2712-HZS-00101A | Z-00101 | 2712-HZS-00101A-3 | Emergency Shutdown Pushbutton | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1702-ST007-0001 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00101 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 15 | DI32
| 795 | 1702 | 2712-HZS-00102A-3 | SDI0010-01R | 2712-HZS-00102A | Z-00102 | 2712-HZS-00102A-3 | Emergency Shutdown Pushbutton | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1702-ST007-0001 | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 New add |  |  | Z-00102 | D3 NKNH21002-1702-ATX.LST-0004_3_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 16 | DI32
| 796 | 1703 | 2713-HZS-00101A-3 | SDI0010-01R | 2713-HZS-00101A | Z-00101 | 2713-HZS-00101A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00101 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 17 | DI32
| 797 | 1703 | 2713-HZS-00701A-3 | SDI0010-01R | 2713-HZS-00701A | Z-00701 | 2713-HZS-00701A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00701 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 18 | DI32
| 798 | 1703 | 2713-HZS-00702A-3 | SDI0010-01R | 2713-HZS-00702A | Z-00702 | 2713-HZS-00702A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-00702 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 19 | DI32
| 799 | 1703 | 2713-HZS-01001A-3 | SDI0010-01R | 2713-HZS-01001A | Z-01001 | 2713-HZS-01001A-3 | Manual confirmation | PUSH BUTTION | 0000-S-RC-C03 | 2490156-1703-ST007-0000 | AUX | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Change "HS" to "HZS" |  |  | Z-01001 | E3 NKNH21002-1703-ATX.LST-0004_4_EN 待出版 | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 20 | DI32
Изм 2026.06.19 New | 800 | 005 | 0005-HZS-10006-3 | SDI0010-01R | - | 0005-Z-1006/2622-I-00001 | 0005-HZS-10006-3 | Title 2307 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 1 | DI32
Изм 2026.06.19 New | 801 | 005 | 0005-HZS-10008-3 | SDI0010-01R | - | 2711-Z-10001 | 0005-HZS-10008-3 | Title 1402 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 2 | DI32
Изм 2026.06.19 New | 802 | 005 | 0005-HZS-10009-3 | SDI0010-01R | - | 2818-Z-00002 | 0005-HZS-10009-3 | Title 2818 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 3 | DI32
Изм 2026.06.19 New | 803 | 005 | 0005-HZS-10010-3 | SDI0010-01R | - | 2311-I-07001 | 0005-HZS-10010-3 | Title 2311 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 4 | DI32
Изм 2026.06.19 New | 804 | 005 | 0005-HZS-10011-3 | SDI0010-01R | - | 2712-Z-10001 | 0005-HZS-10011-3 | Title 1702 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 5 | DI32
Изм 2026.06.19 New | 805 | 005 | 0005-HZS-10012-3 | SDI0010-01R | - | 2713-Z-10001 | 0005-HZS-10012-3 | Title 1703 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 6 | DI32
Изм 2026.06.19 New | 806 | 005 | 0005-HZS-10013-3 | SDI0010-01R | - | 2630-I-26001 | 0005-HZS-10013-3 | Title 2304 ESD-1 Interlock | Push button | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 7 | DI32
Изм 2026.06.19 New | 807 | 2000 | 2000-MOS-10001-3 | SDI0010-01R | - | - | 2000-MOS-10001-3 | OSBL MOS Enabled | Switch | 0000-S-RC-C03 | - | AUX | DIR-VFC | - | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 New add |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 04 | - | A205-04 | - | A206-04 | - | 8 | DI32