## OSBL_IO_List_SCS_v4
Status_Comment | Код | Title | LOOP | TYPNO | Loop No | Logic No | Tag No | Service | Instrument Type | FCS | PID No | Location | I/O Type | Extype | System | Sub System | Auxiliary Instrument | Min | Max | Unit | Min1 | Max1 | Unit1 | LL | L | H | HH | Unit2 | Rev | Remarks | 包设备 | Поле28 | Поле29 | Doc | REV_AK | CABLE No_AK | Discription_AK | Cable type | Beginning | Ending | Length(m) | Color | Pair | Note | Title_AK | Drum No | Power supply voltage | CABLE No_Tecon | MCC substations | Control_cabinet | Mashalling_cabinet | Тег_CPU | Main_Chassis | Redundand_Chassis | Slot | Redundant_slot | Main_module | Main_module2 | Redundant_module | Redundant_module2 | Channel | ModuleType
| 1 | 1401 | 2701-XZY-10101A | SDO0001-01 | 2701-X-10101A | 2701-Z-10001/2701-Z-10004/2701-Z-10101 | 2701-XZY-10101A | Styrene Inlet Switch Valve of 2701-TK-1205A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10101 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 01 | Rev3 JB No. Change | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 20 | DO32P
| 2 | 1401 | 2701-XZZSC-10101A | SDI0010-02R | 2701-X-10101A | - | 2701-XZZSC-10101A | Styrene Inlet Switch Valve of 2701-TK-1205A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 18 | DI32
| 3 | 1401 | 2701-XZZSO-10101A | SDI0010-02R | 2701-X-10101A | - | 2701-XZZSO-10101A | Styrene Inlet Switch Valve of 2701-TK-1205A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 06 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 19 | DI32
| 5 | 1401 | 2701-XZY-10102A | SDO0001-01 | 2701-X-10102A | 2701-Z-10001/2701-Z-10004/2701-Z-10102 | 2701-XZY-10102A | Styrene Outlet Switch Valve of 2701-TK-1205A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 04 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 21 | DO32P
| 6 | 1401 | 2701-XZZSC-10102A | SDI0010-02R | 2701-X-10102A | 2701-Z-10102 | 2701-XZZSC-10102A | Styrene Outlet Switch Valve of 2701-TK-1205A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 04 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 9 | DI32
| 8 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 01 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 0 | AI16H
| 9 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | - | 2701-LZIA-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 10 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | - | 2701-LZAHH-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 11 | 1401 | 2701-LZIA-10101A | SAI1000-01R | 2701-L-10101A | - | 2701-LZALL-10101A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 13 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 08 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 8 | AI16H
| 14 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | - | 2701-LZIA-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 15 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | - | 2701-LZAHH-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 16 | 1401 | 2701-LZIA-10102A | SAI1000-01R | 2701-L-10102A | - | 2701-LZALL-10102A | Remote Liquid Level Gauge of 2701-TK-1205A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
Изм 2026.06.19 Change io type DIR-VFC -> S | 18 | 1401 | 2701-HZS-10001 | SDO0001-01 | 2701-HZS-10001 | 2701-Z-10001 | 2701-HZS-10001 | Fire dike isolation interlock 1 | Soft Push button | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change to soft button |  |  | Z-10001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN
| 19 | 1401 | 2701-HZS-10002 | SDI0010-01R | 2701-HZS-10002 | 2701-Z-10001 | 2701-HZS-10002 | Manual confirmation | PUSH BUTTON | 2000-S-SC-B01 | 2490156-1401-PR007-0101A | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B042/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2701-S-JB-B042 | SIS |  | BK | 01 | Rev3 JB No. Change | 1401 |  |  | 2701-S-JB-B042 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 1 | DI32
Изм 2026.06.19 Change tag 2701-HZS-10007 -> 0005-HZS-10007 | 20 | 005 | 0005-HZS-10007-1 | SDI0010-01R | 0005-HZS-10007 | 2701-Z-10004 | 0005-HZS-10007-1 | Process block interlock (ESD-2) | PUSH BUTTON | 0000-S-RC-C03 | 2490156-1401-PR007-0101A | AUX | DIR-VFC | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change tag no |  |  | Z-10004 | B3 NKNH21002-1401-ATX.LST-0004_4_EN | [15 empty] | 0000-S-RC-C03 | 0000-S-RC-C03 |  | A205 | A206 | 02 | - | A205-02 | - | A206-02 | - | 0 | DI32
| 22 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 02 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 1 | AI16H
| 23 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | - | 2701-LZIA-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 24 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | - | 2701-LZAHH-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 25 | 1401 | 2701-LZIA-10101B | SAI1000-01R | 2701-L-10101B | - | 2701-LZALL-10101B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 27 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | 2701-Z-10101/2701-Z-10102 | 2701-LZT-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 91,51 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10101/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 01 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 13 | AI16H
| 28 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | - | 2701-LZIA-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 29 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | - | 2701-LZAHH-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 30 | 1401 | 2701-LZIA-10102B | SAI1000-01R | 2701-L-10102B | - | 2701-LZALL-10102B | Remote Liquid Level Gauge of 2701-TK-1205B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 32 | 1401 | 2701-XZY-10101B | SDO0001-01 | 2701-X-10101B | 2701-Z-10001/2701-Z-10004/2701-Z-10101 | 2701-XZY-10101B | Styrene Inlet Switch Valve of 2701-TK-1205B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10101 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 02 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 16 | DO32P
| 33 | 1401 | 2701-XZZSC-10101B | SDI0010-02R | 2701-X-10101B | - | 2701-XZZSC-10101B | Styrene Inlet Switch Valve of 2701-TK-1205B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 02 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 20 | DI32
| 34 | 1401 | 2701-XZZSO-10101B | SDI0010-02R | 2701-X-10101B | - | 2701-XZZSO-10101B | Styrene Inlet Switch Valve of 2701-TK-1205B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 07 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 21 | DI32
| 36 | 1401 | 2701-XZY-10102B | SDO0001-01 | 2701-X-10102B | 2701-Z-10001/2701-Z-10004/2701-Z-10102 | 2701-XZY-10102B | Styrene Inlet Switch Valve of 2701-TK-1205B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 05 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 17 | DO32P
| 37 | 1401 | 2701-XZZSC-10102B | SDI0010-02R | 2701-X-10102B | 2701-Z-10102 | 2701-XZZSC-10102B | Styrene Inlet Switch Valve of 2701-TK-1205B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10102 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 11 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 7 | DI32
| 40 | 1401 | 2701-LZIA-10101C | SAI1000-01R | 2701-L-10101C | 2701-Z-10101/2701-Z-10102/2701-Z-10103 | 2701-LZT-10101C | Remote Liquid Level Gauge of 2701-TK-1205S | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10101/10102/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 03 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 2 | AI16H
| 41 | 1401 | 2701-LZIA-10101C | SAI1000-01R | 2701-L-10101C | - | 2701-LZIA-10101C | Remote Liquid Level Gauge of 2701-TK-1205S | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 42 | 1401 | 2701-LZIA-10101C | SAI1000-01R | 2701-L-10101C | - | 2701-LZAH-10101C | Remote Liquid Level Gauge of 2701-TK-1205S | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 44 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | 2701-Z-10101/2701-Z-10102/2701-Z-10103 | 2701-LZT-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 91,51 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10101/10102/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 07 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 15 | AI16H
| 45 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | - | 2701-LZIA-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 46 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | - | 2701-LZAHH-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 47 | 1401 | 2701-LZIA-10102C | SAI1000-01R | 2701-L-10102C | - | 2701-LZALL-10102C | Remote Liquid Level Gauge of 2701-TK-1205S | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 49 | 1401 | 2701-XZY-10101C | SDO0001-01 | 2701-X-10101C | 2701-Z-10001/2701-Z-10004/2701-Z-10101 | 2701-XZY-10101C | Styrene Inlet Switch Valve of 2701-TK-1205S | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10101 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 03 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 22 | DO32P
| 50 | 1401 | 2701-XZZSO-10101C | SDI0010-02R | 2701-X-10101C | - | 2701-XZZSO-10101C | Styrene Inlet Switch Valve of 2701-TK-1205S | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 08 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 17 | DI32
| 51 | 1401 | 2701-XZZSC-10101C | SDI0010-02R | 2701-X-10101C | - | 2701-XZZSC-10101C | Styrene Inlet Switch Valve of 2701-TK-1205S | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 03 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 16 | DI32
| 53 | 1401 | 2701-XZY-10102C | SDO0001-01 | 2701-X-10102C | 2701-Z-10001/2701-Z-10004/2701-Z-10103 | 2701-XZY-10102C | Styrene Inlet Switch Valve of 2701-TK-1205S | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 06 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 18 | DO32P
| 54 | 1401 | 2701-XZZSC-10102C | SDI0010-02R | 2701-X-10102C | 2701-Z-10103 | 2701-XZZSC-10102C | Styrene Inlet Switch Valve of 2701-TK-1205S | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0101C | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10103 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C011/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C011 | SIS | 429 | BU | 05 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C011 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 12 | DI32
| 56 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 04 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 3 | AI16H
| 57 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | - | 2701-LZIA-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 58 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | - | 2701-LZAHH-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 59 | 1401 | 2701-LZIA-10201A | SAI1000-01R | 2701-L-10201A | - | 2701-LZALL-10201A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 61 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 02 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 9 | AI16H
| 62 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | - | 2701-LZIA-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 63 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | - | 2701-LZAHH-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 64 | 1401 | 2701-LZIA-10202A | SAI1000-01R | 2701-L-10202A | - | 2701-LZALL-10202A | Remote Liquid Level Gauge of 2701-TK-1204A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 66 | 1401 | 2701-XZY-10201A | SDO0001-01 | 2701-X-10201A | 2701-Z-10001/2701-Z-10004/2701-Z-10201 | 2701-XZY-10201A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10201 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 01 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 21 | DO32P
| 67 | 1401 | 2701-XZZSO-10201A | SDI0010-02R | 2701-X-10201A | - | 2701-XZZSO-10201A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update instrument type,location,IO type |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 06 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 24 | DI32
| 68 | 1401 | 2701-XZZSC-10201A | SDI0010-02R | 2701-X-10201A | - | 2701-XZZSC-10201A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update instrument type,location,IO type |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 14 | DI32
| 70 | 1401 | 2701-XZY-10202A | SDO0001-01 | 2701-X-10202A | 2701-Z-10001/2701-Z-10004/2701-Z-10202 | 2701-XZY-10202A | Dehydrogenation Mixture Outlet Switch Valve of 2701-TK-1204A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 03 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 16 | DO32P
| 71 | 1401 | 2701-XZZSC-10202A | SDI0010-02R | 2701-X-10202A | 2701-Z-10202 | 2701-XZZSC-10202A | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 1 | Rev1 Update instrument type,location,IO type |  |  | Z-10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 12 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 9 | DI32
| 73 | 1401 | 2701-LZIA-10201B | SAI1000-01R | 2701-L-10201B | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10201B | Remote Liquid Level Gauge of 2701-TK-1204B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 05 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 4 | AI16H
| 74 | 1401 | 2701-LZIA-10201B | SAI1000-01R | 2701-L-10201B | - | 2701-LZIA-10201B | Remote Liquid Level Gauge of 2701-TK-1204B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 76 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | 2701-Z-10201/2701-Z-10202 | 2701-LZT-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 85,383 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10201/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 03 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 14 | AI16H
| 77 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | - | 2701-LZIA-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 78 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | - | 2701-LZAHH-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 79 | 1401 | 2701-LZIA-10202B | SAI1000-01R | 2701-L-10202B | - | 2701-LZALL-10202B | Remote Liquid Level Gauge of 2701-TK-1204B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 81 | 1401 | 2701-XZY-10201B | SDO0001-01 | 2701-X-10201B | 2701-Z-10001/2701-Z-10004/2701-Z-10201 | 2701-XZY-10201B | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10201 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 02 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 17 | DO32P
| 82 | 1401 | 2701-XZZSO-10201B | SDI0010-02R | 2701-X-10201B | - | 2701-XZZSO-10201B | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 07 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 19 | DI32
| 83 | 1401 | 2701-XZZSC-10201B | SDI0010-02R | 2701-X-10201B | - | 2701-XZZSC-10201B | Dehydrogenation Mixture Inlet Switch Valve of 2701-TK-1204B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 02 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 15 | DI32
| 85 | 1401 | 2701-XZY-10202B | SDO0001-01 | 2701-X-10202B | 2701-Z-10001/2701-Z-10004/2701-Z-10202 | 2701-XZY-10202B | Dehydrogenation Mixture Outlet Switch Valve of 2701-TK-1204B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 04 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 19 | DO32P
| 86 | 1401 | 2701-XZZSC-10202B | SDI0010-02R | 2701-X-10202B | 2701-Z-10202 | 2701-XZZSC-10202B | Dehydrogenation Mixture Outlet Switch Valve of 2701-TK-1204B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0102B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10202 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 13 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 11 | DI32
| 88 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 06 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 5 | AI16H
| 89 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | - | 2701-LZIA-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 90 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | - | 2701-LZAH-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 91 | 1401 | 2701-LZIA-10301A | SAI1000-01R | 2701-L-10301A | - | 2701-LZAL-10301A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 93 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 86,387 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 06 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 11 | AI16H
| 94 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | - | 2701-LZIA-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 95 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | - | 2701-LZAHH-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 96 | 1401 | 2701-LZIA-10302A | SAI1000-01R | 2701-L-10302A | - | 2701-LZALL-10302A | Remote Liquid Level Gauge of 2701-TK-1202A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 98 | 1401 | 2701-XZY-10301A | SDO0001-01 | 2701-X-10301A | 2701-Z-10001/2701-Z-10004/2701-Z-10301 | 2701-XZY-10301A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10301 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 05 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 22 | DO32P
| 99 | 1401 | 2701-XZZSO-10301A | SDI0010-02R | 2701-X-10301A | - | 2701-XZZSO-10301A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 08 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 20 | DI32
| 100 | 1401 | 2701-XZZSC-10301A | SDI0010-02R | 2701-X-10301A | - | 2701-XZZSC-10301A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 03 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 16 | DI32
| 102 | 1401 | 2701-XZY-10302A | SDO0001-01 | 2701-X-10302A | 2701-Z-10001/2701-Z-10004/2701-Z-10302 | 2701-XZY-10302A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 07 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 18 | DO32P
| 103 | 1401 | 2701-XZZSC-10302A | SDI0010-02R | 2701-X-10302A | 2701-Z-10302 | 2701-XZZSC-10302A | Ethylbenzene Inlet Switch Valve of 2701-TK-1202A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 11 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 22 | DI32
| 105 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 07 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 6 | AI16H
| 106 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | - | 2701-LZIA-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 107 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | - | 2701-LZAHH-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 108 | 1401 | 2701-LZIA-10301B | SAI1000-01R | 2701-L-10301B | - | 2701-LZALL-10301B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 110 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | 2701-Z-10301/2701-Z-10302 | 2701-LZT-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 86,387 | kPa | 400 | 10650 | mm | - | - | - | - | - | 0 | - |  |  | Z-10301/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 05 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 10 | AI16H
| 111 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | - | 2701-LZIA-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 112 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | - | 2701-LZAHH-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 113 | 1401 | 2701-LZIA-10302B | SAI1000-01R | 2701-L-10302B | - | 2701-LZALL-10302B | Remote Liquid Level Gauge of 2701-TK-1202B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 115 | 1401 | 2701-XZY-10301B | SDO0001-01 | 2701-X-10301B | 2701-Z-10001/2701-Z-10004/2701-Z-10301 | 2701-XZY-10301B | Ethylbenzene Inlet Switch Valve of 2701-TK-1202B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10301 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 06 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 20 | DO32P
| 116 | 1401 | 2701-XZZSO-10301B | SDI0010-02R | 2701-X-10301B | - | 2701-XZZSO-10301B | Ethylbenzene Inlet Switch Valve of 2701-TK-1202B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 09 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 25 | DI32
| 117 | 1401 | 2701-XZZSC-10301B | SDI0010-02R | 2701-X-10301B | - | 2701-XZZSC-10301B | Ethylbenzene Inlet Switch Valve of 2701-TK-1202B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 04 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 17 | DI32
| 119 | 1401 | 2701-XZY-10302B | SDO0001-01 | 2701-X-10302B | 2701-Z-10001/2701-Z-10004/2701-Z-10302 | 2701-XZY-10302B | Ethylbenzene Outlet Switch Valve of 2701-TK-1202B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 08 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 15 | DO32P
| 120 | 1401 | 2701-XZZSC-10302B | SDI0010-02R | 2701-X-10302B | 2701-Z-10302 | 2701-XZZSC-10302B | Ethylbenzene Outlet Switch Valve of 2701-TK-1202B | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0103B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10302 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 12 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 23 | DI32
| 122 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | 2701-Z-10401/2701-Z-10402 | 2701-LZT-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 10650 | mm | 0 | 10650 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10401/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 08 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 7 | AI16H
| 123 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | - | 2701-LZIA-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 124 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | - | 2701-LZAHH-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 125 | 1401 | 2701-LZIA-10401 | SAI1000-01R | 2701-L-10401 | - | 2701-LZALL-10401 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 127 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | 2701-Z-10401/2701-Z-10402 | 2701-LZT-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 86,24 | kPa | 400 | 10400 | mm | - | - | - | - | - | 0 | - |  |  | Z-10401/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C030/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C030 | SIS | 435 | BU | 04 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0005 |  | 2701-S-JB-C030 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 12 | AI16H
| 128 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | - | 2701-LZIA-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 129 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | - | 2701-LZAHH-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 130 | 1401 | 2701-LZIA-10402 | SAI1000-01R | 2701-L-10402 | - | 2701-LZALL-10402 | Remote Liquid Level Gauge of 2701-TK-1201 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 132 | 1401 | 2701-XZY-10401 | SDO0001-01 | 2701-X-10401 | 2701-Z-10001/2701-Z-10004/2701-Z-10401 | 2701-XZY-10401 | Benzene Inlet Switch Valve of 2701-TK-1201 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10401 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D019/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D019 | SIS | 409 | BK | 09 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0003 |  | 2701-S-JB-D019 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 23 | DO32P
| 133 | 1401 | 2701-XZZSO-10401 | SDI0010-02R | 2701-X-10401 | - | 2701-XZZSO-10401 | Benzene Inlet Switch Valve of 2701-TK-1201 | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 10 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 21 | DI32
| 134 | 1401 | 2701-XZZSC-10401 | SDI0010-02R | 2701-X-10401 | - | 2701-XZZSC-10401 | Benzene Inlet Switch Valve of 2701-TK-1201 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C012/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C012 | SIS | 409 | BU | 05 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0003 |  | 2701-S-JB-C012 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 18 | DI32
| 136 | 1401 | 2701-XZY-10402 | SDO0001-01 | 2701-X-10402 | 2701-Z-10001/2701-Z-10004/2701-Z-10402 | 2701-XZY-10402 | Benzene Outlet Switch Valve of 2701-TK-1201 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10001/10004/10402 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D018/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D018 | SIS | 429 | BK | 07 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0002 |  | 2701-S-JB-D018 |  | 2000-S-SC-B01 | 2000-S-MC-B05F |  | A13 | A14 | 05 | 06 | A13-05 | A13-06 | A14-05 | A14-06 | 19 | DO32P
| 137 | 1401 | 2701-XZZSC-10402 | SDI0010-02R | 2701-X-10402 | - | 2701-XZZSC-10402 | Benzene Outlet Switch Valve of 2701-TK-1201 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0104 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 14 | Rev1 New add | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 4 | DI32
| 139 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | 2701-Z-10501/2701-Z-10502 | 2701-LZT-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 11500 | mm | 0 | 11500 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10501/10502 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 09 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 8 | AI16H
| 140 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | - | 2701-LZIA-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | 0 | 11500 | mm | 0 | 11500 | mm | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 141 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | - | 2701-LZAHH-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 142 | 1401 | 2701-LZIA-10501 | SAI1000-01R | 2701-L-10501 | - | 2701-LZALL-10501 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 144 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | 2701-Z-10501/2701-Z-10502 | 2701-LZT-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 93,551 | kPa | 400 | 11500 | mm | - | - | - | - | - | 0 | - |  |  | Z-10501/10502 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 07 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 1 | AI16H
| 145 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | - | 2701-LZIA-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 146 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | - | 2701-LZAHH-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 147 | 1401 | 2701-LZIA-10502 | SAI1000-01R | 2701-L-10502 | - | 2701-LZALL-10502 | Remote Liquid Level Gauge of 2701-TK-1203 | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 149 | 1401 | 2701-XZY-10501 | SDO0001-01 | 2701-X-10501 | 2701-Z-10002/2701-Z-10004/2701-Z-10501 | 2701-XZY-10501 | Off-Spec Ethylbenzene Inlet Switch Valve of 2701-TK-1203 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10501 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 02 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 3 | DO32P
| 150 | 1401 | 2701-XZZSO-10501 | SDI0010-02R | 2701-X-10501 | - | 2701-XZZSO-10501 | Off-Spec Ethylbenzene Inlet Switch Valve of 2701-TK-1203 | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 06 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 2 | DI32
| 151 | 1401 | 2701-XZZSC-10501 | SDI0010-02R | 2701-X-10501 | - | 2701-XZZSC-10501 | Off-Spec Ethylbenzene Inlet Switch Valve of 2701-TK-1203 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 01 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 14 | DI32
| 153 | 1401 | 2701-XZY-10502 | SDO0001-01 | 2701-X-10502 | 2701-Z-10002/2701-Z-10004/2701-Z-10502 | 2701-XZY-10502 | Off-Spec Ethylbenzene Outlet Switch Valve of 2701-TK-1203 | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10502 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 03 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 10 | DO32P
| 154 | 1401 | 2701-XZZSC-10502 | SDI0010-02R | 2701-X-10502 | - | 2701-XZZSC-10502 | Off-Spec Ethylbenzene Outlet Switch Valve of 2701-TK-1203 | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 03 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 6 | DI32
Изм 2026.06.19 Change io type DIR-VFC -> S | 156 | 1401 | 2701-HZS-10003 | SDO0001-01 | 2701-HZS-10003 | 2701-Z-10002 | 2701-HZS-10003 | Fire dike isolation interlock 2 | Soft Push button | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Rev4 change to soft button |  |  | Z-10002 | B3 NKNH21002-1401-ATX.LST-0004_4_EN
| 157 | 1401 | 2701-HZS-10004 | SDI0010-01R | 2701-HZS-10004 | 2701-Z-10002 | 2701-HZS-10004 | Manual confirmation | PUSH BUTTON | 2000-S-SC-B01 | 2490156-1401-PR007-0105 | Field | DIR-VFC | Ex.d | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B042/SIS | 8x2x1.0mm2,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 8x2x1.0 | 2701-S-JB-B042 | SIS |  | BK | 02 | Rev3 JB No. Change | 1401 |  |  | 2701-S-JB-B042 |  | 2000-S-SC-B01 | 2000-S-MC-B03R |  | A13 | A14 | 00 | - | A13-00 | - | A14-00 | - | 2 | DI32
| 159 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 8250 | mm | 0 | 8250 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 10 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 9 | AI16H
| 160 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | - | 2701-LZIA-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 161 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | - | 2701-LZAHH-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 162 | 1401 | 2701-LZIA-10601A | SAI1000-01R | 2701-L-10601A | - | 2701-LZALL-10601A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 164 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 62,916 | kPa | 400 | 7900 | mm | - | - | - | - | - | 0 | - |  |  | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 05 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 5 | AI16H
| 165 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | - | 2701-LZIA-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 166 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | - | 2701-LZAHH-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 167 | 1401 | 2701-LZIA-10602A | SAI1000-01R | 2701-L-10602A | - | 2701-LZALL-10602A | Remote Liquid Level Gauge of 2701-TK-1206A | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 169 | 1401 | 2701-XZY-10601A | SDO0001-01 | 2701-X-10601A | 2701-Z-10002/2701-Z-10004/2701-Z-10601 | 2701-XZY-10601A | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10601 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 04 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 4 | DO32P
| 170 | 1401 | 2701-XZZSO-10601A | SDI0010-02R | 2701-X-10601A | - | 2701-XZZSO-10601A | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206A | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 07 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 3 | DI32
| 171 | 1401 | 2701-XZZSC-10601A | SDI0010-02R | 2701-X-10601A | - | 2701-XZZSC-10601A | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 02 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 4 | DI32
| 173 | 1401 | 2701-XZY-10602A | SDO0001-01 | 2701-X-10602A | 2701-Z-10002/2701-Z-10004/2701-Z-10602 | 2701-XZY-10602A | Benzene/Toluene Mixture Outlet Switch Valve of 2701-TK-1206A | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 06 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 5 | DO32P
| 174 | 1401 | 2701-XZZSC-10602A | SDI0010-02R | 2701-X-10602A | 2701-Z-10602 | 2701-XZZSC-10602A | Benzene/Toluene Mixture Outlet Switch Valve of 2701-TK-1206A | VALVE SWITCH CLOSE | 2000-S-SC-B01 | 2490156-1401-PR007-0106A | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C010/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C010 | SIS | 387 | BU | 04 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0002 |  | 2701-S-JB-C010 |  | 2000-S-SC-B01 | 2000-S-MC-B02R |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 1 | DI32
| 176 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | RADAR LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | AIR-LP | Ex.d | SIS | - | - | 0 | 8250 | mm | 0 | 8250 | mm | - | - | - | - | - | 4 | Rev4 Change to loop power |  | Xinhui | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-B037/SIS | 16x2x2.5mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-DJYP3VP3 16x2x2.5 | 2701-S-JB-B037 | SIS | 405 | BK | 11 | Rev1 change cable length, colour, type | 1401 | 1401-WDZAN-DJYJP3YP3 16x2x2.5-0001 |  | 2701-S-JB-B037 |  | 2000-S-SC-B01 | 2000-S-MC-B03F |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 10 | AI16H
| 177 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | - | 2701-LZIA-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 178 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | - | 2701-LZAHH-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 179 | 1401 | 2701-LZIA-10601B | SAI1000-01R | 2701-L-10601B | - | 2701-LZALL-10601B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 181 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | 2701-Z-10601/2701-Z-10602 | 2701-LZT-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | DIFFERENTIAL PRESSURE LEVEL TRANSMITTER | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | AIR(I)-LP | Ex.i | SIS | - | B | 0 | 62,916 | kPa | 400 | 7900 | mm | - | - | - | - | - | 0 | - |  |  | Z-10601/10602 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 | 1 | 2701-S-JB-C007/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C007 | SIS | 387 | BU | 06 | Rev1 change cable length | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C007 |  | 2000-S-SC-B01 | 2000-S-MC-B01F |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 2 | AI16H
| 182 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | - | 2701-LZIA-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | Indicate & Alarm:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 183 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | - | 2701-LZAHH-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 184 | 1401 | 2701-LZIA-10602B | SAI1000-01R | 2701-L-10602B | - | 2701-LZALL-10602B | Remote Liquid Level Gauge of 2701-TK-1206B | ALARM:SIS | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | SIS | S | - | SIS | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版
| 186 | 1401 | 2701-XZY-10601B | SDO0001-01 | 2701-X-10601B | 2701-Z-10002/2701-Z-10004/2701-Z-10601 | 2701-XZY-10601B | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206B | Solenoid valve | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | DOR-P | Ex.d | SIS | - | R | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  | Z-10002/10004/10601 | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-D017/SIS | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | NH-KYJVP3 37x2.5mm2 | 2701-S-JB-D017 | SIS | 387 | BK | 05 |  | 1401 | 1401-WDZAN-KYJYP3 37x2.5-0001 |  | 2701-S-JB-D017 |  | 2000-S-SC-B01 | 2000-S-MC-B04R |  | A13 | A14 | 03 | 04 | A13-03 | A13-04 | A14-03 | A14-04 | 6 | DO32P
| 187 | 1401 | 2701-XZZSO-10601B | SDI0010-02R | 2701-X-10601B | - | 2701-XZZSO-10601B | Benzene/Toluene Mixture Inlet Switch Valve of 2701-TK-1206B | VALVE SWITCH OPEN | 2000-S-SC-B01 | 2490156-1401-PR007-0106B | Field | DIR(I)-NAMUR | Ex.i | SIS | - | B | - | - | - | - | - | - | - | - | - | - | - | 0 | - |  |  |  | B3 NKNH21002-1401-ATX.LST-0004_4_EN 待出版 |  | 2701-S-JB-C009/SIS | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | NH-IA-DJYP3VP3 16x2x1.0 | 2701-S-JB-C009 | SIS | 397 | BU | 08 |  | 1401 | 1401-WDZAN-IA-DJYJP3YP3 16x2x1.0-0001 |  | 2701-S-JB-C009 |  | 2000-S-SC-B01 | 2000-S-MC-B01R |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 5 | DI32